## Cover Sheet
CALCULATION OF REASONABLY EFFICIENT COMPETITOR COSTS
DISCLAIMER:
The Excel Spreadsheet has been prepared for the Independent Pricing and Regulatory Tribunal as part of its review into wholesale water and sewerage prices. The analysis and information provided in this Excel Spreadsheet is derived in whole or in part from information prepared by a range of parties other than Oakley Greenwood. Oakley Greenwood explicitly disclaims liability for any errors or omissions in that information, or any other aspect of the validity of that information. We also disclaim liability for the use of any information in this report by any party for any purpose other than the intended purpose.
DESCRIPTION OF SPREADSHEET:
This Excel Spreadsheet sets out benchmark unit rates for a reasonably efficient competitor seeking to enter the water and/or sewerage industries. We have sought to indicate whether certain factors would influence the costs of each of the asset categories and then used these benchmark unit rates in a number of examples scenarios to demonstrate the likely cost to be faced by a new entrant seeking to provide water and/or sewerage services. The assumptions that we have used to cost the example scenarios are contained in the tabs following Example Scenario. An associated report "Calculation of Reasonably Efficient Competitor Costs" also prepared for the Independent Pricing and Regulatory Tribunal should be read in conjunction with this spreadsheet.

## Benchmark Unit Rates
Inflation Factor
103.5%
BENCHMARK UNIT RATES
|  | Service | Asset | Standardised Unit | Asset Characteristics |  |  | Factors that Influence Characteristics |  |  |  |  | Comments
[5 empty] | Value per Unit | Expected Life | Lifecycle Opex | Economies of Scale | Economies of Scope | Topography | Geotechnical | Delivery of Service
| FOR EXAMPLE | Water Retail | 20mm meter | Each | 500 | 12 years | Nil. To be managed by property owner | The density and the size of development is unlikely to have an impact on the unit cost. | As the water meter is generally required to be installed by licenced plumbers, thus it is unlikely to have an impact on the unit cost | The topography is unlikely to have an impact on the unit cost of 20mm meters | The geotechnical condition of the ground is unlikely to have an impact on the unit cost as it is likely to be installed above ground | Different delivery options may impact on factors such as warehousing costs, however it is unlikely to be a material impact on this high level analysis. | Based on $200 for unit and $300 for installation
|  | Water Retail | Billing Services | Per customer, per month | $2-$4 | NA | Only Opex | The range provided is based on the number of customers that would be serviced by the new entrant. The lower end of the range ($2) would represent a higher customer base, while the upper end of the range ($4) would represent a smaller customer base. | There would be economies of scope for billing services - as costs for providing billing services for water-only, wastewater-only or a combined water and wastewater service would be the same (assuming the same number of customers). | No impact on the unit rate of this service | No impact on the unit rate of this service | Given upfront costs of establishing these retail services, we have assumed that these services would be more efficiently provided through an external service provider | Based on information provided by external managed service provider.
|  | Water Retail | Call Centre Services | Per customer, per month | 4 | NA | Only Opex | There are unlikely to be material differences in the unit rates for the size of customers for call centre services. | There are economies of scope in call centre costs for providing wastewater services in addition to water services as the additional call centre costs for wastewater services would be expected to be lower. | No impact on the unit rate of this service | No impact on the unit rate of this service | Given upfront costs of establishing these retail services, we have assumed that these services would be more efficiently provided through an external service provider | Based on information provided by external managed service provider and industry knowledge.
|  | Water Retail | Outbound Customer Communications | Per customer, per month | $0.50-$1 | NA | Only Opex | The range provided is based on the number of customers that would be serviced by the new entrant. The lower end of the range ($0.50) would represent a higher customer base, while the upper end of the range ($1) would represent a smaller customer base. | No impact on the unit rate of this service | No impact on the unit rate of this service | No impact on the unit rate of this service | Given upfront costs of establishing these retail services, we have assumed that these services would be more efficiently provided through an external service provider | Based on information provided by external managed service provider.
|  | Water Retail | Other Retail Services | Per customer, per month | $0.50-$1 | NA | Only Opex | The range provided is based on the number of customers that would be serviced by the new entrant. The lower end of the range ($0.50) would represent a higher customer base, while the upper end of the range ($1) would represent a smaller customer base. | No impact on the unit rate of this service | No impact on the unit rate of this service | No impact on the unit rate of this service | Given upfront costs of establishing these retail services, we have assumed that these services would be more efficiently provided through an external service provider | Based on information provided by external managed service provider and industry knowledge.
|  | Wastewater Retail | Boundary Traps | Each | 1000 |  | Nil. To be managed by property owner | Nil assumed to be installed / constructed by property developer | Nil assumed to be installed / constructed by property developer | Nil assumed to be installed / constructed by property developer | Nil assumed to be installed / constructed by property developer |  | Assumed
|  | Wastewater Retail | DN20 - Water Service Connection | Metre | 64.17 | Pipe: 100 years Valves: 30 years | $2 / metre | The density and the size of development is unlikely to have an impact on the unit cost. | As the water service connection is generally required to be installed by licenced plumbers, thus it is unlikely to have an impact on the unit cost | The topography is unlikely to have an impact as the average depth of pipe is similar in flat and undulated terrains. | Ground condition such as rock excavation, contaminated soil, water charged ground and bearing capacity is likely to have an impact on the unit cost. Encountering rock in trench installation can increase the cost by 20% to 5 times pending on the strength and level of the rock in the pipe trench. |  | Asset life based on Water Supply Code of Australia Unit rate based on DN50 uPVC - Water pipe Opex based on "2013-14 Water Supply and Sewerage NSW Benchmarking Report" Benchmarking cost data, published by Department of Primary Industries, increased to 2016 prices with CPI of 3.5%
|  | Water Reticulation | DN50 uPVC - Water | Metre | 64.17 | Pipe: 100 years Valves: 30 years | $2 / metre | The density and the size of development is unlikely to have an impact on the unit cost. | Capex cost may be lower if utility services (such as water, sewer, stormwater) can be installed by a single civil contractor. | The topography is unlikely to have an impact on the unit cost as the average depth of pipe is similar in flat and undulated terrains. | Ground condition such as rock excavation, contaminated soil, water charged ground and bearing capacity is likely to have an impact on the unit cost. Encountering rock in trench installation can increase the cost by 20% to 5 times pending on the strength and level of the rock in the pipe trench. |  | Asset life based on Water Supply Code of Australia For water reticulation networks, the typical spacing for valves is around 200m, depending on the complexity of the system. Based on this, it is estimated that approximately 5-20% of pipe-related capex is related to valves. Rates are based on "NSW Reference Rates Manual - Valuation of water supply, sewerage and stormwater assets", published by Department of Primary Industries - Office of Water, 2014, increased to 2016 prices with CPI of 3.5% Opex based on "2013-14 Water Supply and Sewerage NSW Benchmarking Report" Benchmarking cost data, published by Department of Primary Industries, increased to 2016 prices with CPI of 3.5%
|  | Water Reticulation | DN80 uPVC - Water | Metre | 82.8 | Pipe: 100 years Valves: 30 years | $2 / metre | Denser development may assist with reducing the length of pipe required, however, it may require larger pipe size which has a higher unit cost | Capex cost may be lower if utility services (such as water, sewer, stormwater) can be installed by a single civil contractor. | The topography is unlikely to have an impact on the unit cost as the average depth of pipe is similar in flat and undulated terrains. | Ground condition such as rock excavation, contaminated soil, water charged ground and bearing capacity is likely to have an impact on the unit cost. Encountering rock in trench installation can increase the cost by 20% to 5 times pending on the strength and level of the rock in the pipe trench. |  | Asset life based on Water Supply Code of Australia For water reticulation networks, the typical spacing for valves is around 200m, depending on the complexity of the system. Based on this, it is estimated that approximately 5-20% of pipe-related capex is related to valves. Rates are based on "NSW Reference Rates Manual - Valuation of water supply, sewerage and stormwater assets", published by Department of Primary Industries - Office of Water, 2014, increased to 2016 price with CPI of 3.5% Opex based on "2013-14 Water Supply and Sewerage NSW Benchmarking Report" Benchmarking cost data, published by Department of Primary Industries, increased to 2016 prices with CPI of 3.5%
CPI | 1.035 | Water Reticulation | DN100 DICL - Brownfield - Water | Metre | 209.07 | Pipe: 100 years Valves: 30 years | $2 / metre | Denser development may assist with reducing the length of pipe required, however, it may require larger pipe size which has a higher unit cost | Capex cost may be lower if utility services (such as water, sewer, stormwater) can be installed by a single civil contractor. | The topography is unlikely to have an impact on the unit cost as the average depth of pipe is similar in flat and undulated terrains. | Ground condition such as rock excavation, contaminated soil, water charged ground and bearing capacity is likely to have an impact on the unit cost. Encountering rock in trench installation can increase the cost by 20% to 5 times pending on the strength and level of the rock in the pipe trench. |  | Asset life based on Water Supply Code of Australia For water reticulation networks, the typical spacing for valves is around 200m, depending on the complexity of the system. Based on this, it is estimated that approximately 5-20% of pipe-related capex is related to valves. 'Unit rate based on minimum pipe installation depth as per Water Supply Code of Australia (typical 600-750mm, laid in roadway). Rates are based on "NSW Reference Rates Manual - Valuation of water supply, sewerage and stormwater assets", published by Department of Primary Industries - Office of Water, 2014, increased to 2016 prices with CPI of 3.5% For brownfield installation, additional cost of moderate construction difficulty has been applied (e.g. existing services) Opex based on "2013-14 Water Supply and Sewerage NSW Benchmarking Report" Benchmarking cost data, published by Department of Primary Industries, increased to 2016 prices with CPI of 3.5%
|  | Water Reticulation | DN150 DICL - Brownfield - Water | Metre | 270.135 | Pipe: 100 years Valves: 30 years | $2 / metre | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN200 DICL - Brownfield - Water | Metre | 342.585 | Pipe: 100 years Valves: 30 years | $2 / metre | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN250 DICL - Brownfield - Water | Metre | 405.72 | Pipe: 100 years Valves: 30 years | $2 / metre | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN300 DICL - Brownfield - Water | Metre | 478.17 | Pipe: 100 years Valves: 30 years | $2 / metre | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN375 DICL - Brownfield - Water | Metre | 612.72 | Pipe: 100 years Valves: 30 years | $2 / metre | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN100 DICL - Greenfield - Water | Metre | 165.6 | Pipe: 100 years Valves: 30 years | $2 / metre | Denser development may assist with reducing the length of pipe required, however, it may require larger pipe size which has a higher unit cost | Capex cost may be lower if utility services (such as water, sewer, stormwater) can be installed by a single civil contractor. | The topography is unlikely to have an impact on the unit cost as the average depth of pipe is similar in flat and undulated terrains. | Ground condition such as rock excavation, contaminated soil, water charged ground and bearing capacity is likely to have an impact on the unit cost. Encountering rock in trench installation can increase the cost by 20% to 5 times pending on the strength and level of the rock in the pipe trench. |  | Asset life based on Water Supply Code of Australia For water reticulation networks, the typical spacing for valves is around 200m, depending on the complexity of the system. Based on this, it is estimated that approximately 5-20% of pipe-related capex is related to valves. 'Unit rate based on minimum pipe installation depth as per Water Supply Code of Australia (typical 600-750mm, laid in roadway). Rates are based on "NSW Reference Rates Manual - Valuation of water supply, sewerage and stormwater assets", published by Department of Primary Industries - Office of Water, 2014, increased to 2016 prices with CPI of 3.5% Opex based on "2013-14 Water Supply and Sewerage NSW Benchmarking Report" Benchmarking cost data, published by Department of Primary Industries, increased to 2016 prices with CPI of 3.5%
|  | Water Reticulation | DN150 DICL - Greenfield - Water | Metre | 207 | Pipe: 100 years Valves: 30 years | $2 / metre | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN200 DICL - Greenfield - Water | Metre | 258.75 | Pipe: 100 years Valves: 30 years | $2 / metre | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN250 DICL - Greenfield - Water | Metre | 300.15 | Pipe: 100 years Valves: 30 years | $2 / metre | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN300 DICL - Greenfield - Water | Metre | 351.9 | Pipe: 100 years Valves: 30 years | $2 / metre | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN375 DICL - Greenfield - Water | Metre | 445.05 | Pipe: 100 years Valves: 30 years | $2 / metre | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN450 DICL - Greenfield - Water | Metre | 527.85 | Pipe: 100 years Valves: 30 years | $2 / metre | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN100 - Brownfield - Sewer | Metre | 267.03 | Pipe: 100 years Maint Struct: 100 years | $3 / metre | Denser development may assist with reducing the length of pipe required, however, it may require larger pipe size which has a higher unit cost | Capex cost may be lower if utility services (such as water, sewer, stormwater) can be installed by a single civil contractor. | The topography is likely to have an impact on the unit cost as the sewer gravity main would have a deeper average depth in flatter terrain compared to undulating terrain. Pending on the installation depth of the sewer gravity main, the unit cost could double to 3 times for a depth up to 4.5m | Ground condition such as rock excavation, contaminated soil, water charged ground and bearing capacity is likely to have an impact on the unit cost. Encountering rock in trench installation can increase the cost by 20% to 5 times pending on the strength and level of the rock in the pipe trench. |  | Asset life based on Sewerage Code of Australia 'Unit rate based on minimum pipe installation depth as per Sewerage Code of Australia (typical 1.5m to 3.0m, laid in roadway). Rates are based on "NSW Reference Rates Manual - Valuation of water supply, sewerage and stormwater assets", published by Department of Primary Industries - Office of Water, 2014, increased to 2016 prices with CPI of 3.5% For brownfield installation, additional cost of moderate construction difficulty has been applied (e.g. existing services) Opex based on "2013-14 Water Supply and Sewerage NSW Benchmarking Report" Benchmarking cost data, published by Department of Primary Industries, increased to 2016 prices with CPI of 3.5%
|  | Wastewater Reticulation - Gravity | DN150 - Brownfield - Sewer | Metre | 324.99 | Pipe: 100 years Maint Struct: 100 years | $3 / metre | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN225 - Brownfield - Sewer | Metre | 431.595 | Pipe: 100 years Maint Struct: 100 years | $3 / metre | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN300 - Brownfield - Sewer | Metre | 568.215 | Pipe: 100 years Maint Struct: 100 years | $3 / metre | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN375 - Brownfield - Sewer | Metre | 740.025 | Pipe: 100 years Maint Struct: 100 years | $3 / metre | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN450 - Brownfield - Sewer | Metre | 903.555 | Pipe: 100 years Maint Struct: 100 years | $3 / metre | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN500 - Brownfield - Sewer | Metre | 1041.21 | Pipe: 100 years Maint Struct: 100 years | $3 / metre | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN600 - Brownfield - Sewer | Metre | 1315.485 | Pipe: 100 years Maint Struct: 100 years | $3 / metre | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN100 - Greenfield - Sewer | Metre | 223.56 | Pipe: 100 years Maint Struct: 100 years | $3 / metre | Denser development may assist with reducing the length of pipe required, however, it may require larger pipe size which has a higher unit cost | Capex cost may be lower if utility services (such as water, sewer, stormwater) can be installed by a single civil contractor. | The topography is likely to have an impact on the unit cost as cost of installation increases with the deep of installation. The sewer gravity main would have a deeper average depth in flatter terrain compare to an undulated terrain. Pending on the installation depth of the sewer gravity main, the unit cost could double to 3 times for a depth up to 4.5m | Ground condition such as rock excavation, contaminated soil, water charged ground and bearing capacity is likely to have an impact on the unit cost. Encountering rock in trench installation can increase the cost by 20% to 5 times pending on the strength and level of the rock in the pipe trench. |  | Asset life based on Sewerage Code of Australia 'Unit rate based on minimum pipe installation depth as per Sewerage Code of Australia (typical 1.5m to 3.0m, laid in roadway). Rates are based on "NSW Reference Rates Manual - Valuation of water supply, sewerage and stormwater assets", published by Department of Primary Industries - Office of Water, 2014, increased to 2016 prices with CPI of 3.5% Opex based on "2013-14 Water Supply and Sewerage NSW Benchmarking Report", published by Department of Primary Industries, increased to 2016 prices with CPI of 3.5%
|  | Wastewater Reticulation - Gravity | DN150 - Greenfield - Sewer | Metre | 261.855 | Pipe: 100 years Maint Struct: 100 years | $3 / metre | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN225 - Greenfield - Sewer | Metre | 326.025 | Pipe: 100 years Maint Struct: 100 years | $3 / metre | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN300 - Greenfield - Sewer | Metre | 441.945 | Pipe: 100 years Maint Struct: 100 years | $3 / metre | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN375 - Greenfield - Sewer | Metre | 572.355 | Pipe: 100 years Maint Struct: 100 years | $3 / metre | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN450 - Greenfield - Sewer | Metre | 693.45 | Pipe: 100 years Maint Struct: 100 years | $3 / metre | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN500 - Greenfield - Sewer | Metre | 802.125 | Pipe: 100 years Maint Struct: 100 years | $3 / metre | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN600 - Greenfield - Sewer | Metre | 1035 | Pipe: 100 years Maint Struct: 100 years | $3 / metre | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | DN100 DICL - Sewer Pressure Pipe | Metre | 119.025 | Pipe: 100 years Valves: 30 years | $3 / metre | Denser development may assist with reducing the length of pipe required, however, it may require larger pipe size which has a higher unit cost | Capex cost may be lower if utility services (such as water, sewer, stormwater) can be installed by a single civil contractor. | The topography is unlikely to have an impact on the unit cost as the average depth of pipe is similar in flat and undulated terrains. | Ground condition such as rock excavation, contaminated soil, water charged ground and bearing capacity is likely to have an impact on the unit cost. Encountering rock in trench installation can increase the cost by 20% to 5 times pending on the strength and level of the rock in the pipe trench. |  | Asset life based on Sewerage Code of Australia 'Unit rate based on minimum pipe installation depth as per Sewerage Code of Australia (typical 600-750mm, laid in roadway). Rates are based on "NSW Reference Rates Manual - Valuation of water supply, sewerage and stormwater assets", published by Department of Primary Industries - Office of Water, 2014, increased to 2016 prices with CPI of 3.5% Opex based on "2013-14 Water Supply and Sewerage NSW Benchmarking Report", published by Department of Primary Industries, increased to 2016 prices with CPI of 3.5%
|  | Wastewater Reticulation - Pressure | DN100 DICL - Sewer Pressure Pipe | Metre | 119.025 | Pipe: 100 years Valves: 30 years | $3 / metre | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | DN150 DICL - Sewer Pressure Pipe | Metre | 165.6 | Pipe: 100 years Valves: 30 years | $3 / metre | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | DN200 DICL - Sewer Pressure Pipe | Metre | 196.65 | Pipe: 100 years Valves: 30 years | $3 / metre | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | DN250 DICL - Sewer Pressure Pipe | Metre | 243.225 | Pipe: 100 years Valves: 30 years | $3 / metre | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | DN300 DICL - Sewer Pressure Pipe | Metre | 243.225 | Pipe: 100 years Valves: 30 years | $3 / metre | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | DN375 DICL - Sewer Pressure Pipe | Metre | 243.225 | Pipe: 100 years Valves: 30 years | $3 / metre | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | Sewerage Pump - 10L/s | Each | 331200 | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 15-25 years | $14,490 / each | Unlikely to have an impact on the unit cost as the sizing of the pump station is independent of the density | Capex cost may be lower if sewerage pumping station and unity services can be constructed together. Other factor such as sourcing off-the-shelf pump skid may also reduce the Capex Cost | The topography is unlikely to have an impact on the unit cost. | On the basis that, the sewer pump station is a wet well (typically 5m-10m deep), the ground condition such as rock excavation, contaminated soil, water charged ground and bearing capacity is likely to have an impact on the unit cost. |  | Asset life based on Sewage Pumping Station Code of Australia Rates are based on "NSW Reference Rates Manual - Valuation of water supply, sewerage and stormwater assets", published by Department of Primary Industries - Office of Water, 2014, increased to 2016 prices with CPI of 3.5% Opex based on "2013-14 Water Supply and Sewerage NSW Benchmarking Report" Benchmarking cost data, published by Department of Primary Industries, increased to 2016 prices with CPI of 3.5%
|  | Wastewater Reticulation - Pressure | Sewerage Pump - 20L/s | Each | 434700 | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 15-25 years | $14,490 / each | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | Sewerage Pump - 30L/s | Each | 548550 | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 15-25 years | $14,490 / each | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | Sewerage Pump - 40L/s | Each | 652050 | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 15-25 years | $14,490 / each | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | Sewerage Pump - 50L/s | Each | 745200 | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 15-25 years | $14,490 / each | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | Sewerage Pump - 60L/s | Each | 828000 | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 15-25 years | $14,490 / each | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | Sewerage Pump - 80L/s | Each | 983250 | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 15-25 years | $14,490 / each | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | Sewerage Pump - 100L/s | Each | 1107450 | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 15-25 years | $14,490 / each | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | Sewerage Pump - 140L/s | Each | 1345500 | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 15-25 years | $14,490 / each | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | Sewerage Pump - 180L/s | Each | 1552500 | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 15-25 years | $14,490 / each | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | Sewerage Pump - 200L/s | Each | 1656000 | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 15-25 years | $14,490 / each | See above | See above | See above | See above |  | See above
|  | Water Reticulation | Water Pumping Station - 10kW | Each | 82800 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $26,910 / each | Unlikely to have an impact on the unit cost as the sizing of the pump station is independent of the denser | Capex cost may be lower if water pumping station and water reservoir can be constructed together. Other factor such as sourcing off-the-shelf pump skid may also reduce the Capex Cost | On the basis that, the pumping station is an above ground structure, the topography is unlikely to have an impact on the unit cost. | On the basis that, the pumping station is above ground, the ground condition such as rock excavation, contaminated soil, water charged ground and bearing capacity is likely to have an impact on the unit cost. |  | Asset life based on Water Supply Code of Australia Rates are based on "NSW Reference Rates Manual - Valuation of water supply, sewerage and stormwater assets", published by Department of Primary Industries - Office of Water, 2014, increased to 2016 prices with CPI of 3.5% Opex based on "2013-14 Water Supply and Sewerage NSW Benchmarking Report" Benchmarking cost data, published by Department of Primary Industries, increased to 2016 prices with CPI of 3.5%
|  | Water Reticulation | Water Pumping Station - 20kW | Each | 119025 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $26,910 / each | See above | See above | See above | See above |  | See above
|  | Water Reticulation | Water Pumping Station - 30kW | Each | 144900 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $26,910 / each | See above | See above | See above | See above |  | See above
|  | Water Reticulation | Water Pumping Station - 50kW | Each | 196650 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $26,910 / each | See above | See above | See above | See above |  | See above
|  | Water Reticulation | Water Pumping Station - 100kW | Each | 382950 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $26,910 / each | See above | See above | See above | See above |  | See above
|  | Water Reticulation | Water Service Reservoirs - 0.5ML | Each | 408825 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $10 / property | Unlikely to have an impact on the unit cost as the sizing of the pump station is independent of the density | Capex cost may be lower if water reservoir and water pumping station can be constructed together. | On the basis that, the reservoir is an above ground structure, the topography is unlikely to have an impact on the unit cost. | On the basis that, the reservoir is above ground, the ground condition such as rock excavation, contaminated soil, water charged ground and bearing capacity is likely to have an impact on the unit cost. |  | Asset life based on Water Supply Code of Australia Rates are based on "NSW Reference Rates Manual - Valuation of water supply, sewerage and stormwater assets", published by Department of Primary Industries - Office of Water, 2014, increased to 2016 prices with CPI of 3.5% Opex based on "2013-14 Water Supply and Sewerage NSW Benchmarking Report" Benchmarking cost data, published by Department of Primary Industries, increased to 2016 prices with CPI of 3.5%
|  | Water Reticulation | Water Service Reservoirs - 1ML | Each | 610650 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $10 / property | See above | See above | See above | See above |  | See above
|  | Water Reticulation | Water Service Reservoirs - 2ML | Each | 869400 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $10 / property | See above | See above | See above | See above |  | See above
|  | Water Reticulation | Water Service Reservoirs - 4ML | Each | 1190250 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $10 / property | See above | See above | See above | See above |  | See above
|  | Water Reticulation | Water Service Reservoirs - 5ML | Each | 1366200 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $10 / property | See above | See above | See above | See above |  | See above
|  | Water Reticulation | Water Service Reservoirs - 8ML | Each | 1863000 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $10 / property | See above | See above | See above | See above |  | See above
|  | Water Reticulation | Water Service Reservoirs - 10ML | Each | 2173500 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $10 / property | See above | See above | See above | See above |  | See above
|  | Water Reticulation | Water Service Reservoirs - 15ML | Each | 2949750 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $10 / property | See above | See above | See above | See above |  | See above

## Example Scenarios
EXAMPLE SCENARIO COST INFORMATION
[5 empty] | Example 1: 2,000 20mm equivalent brownfield development |  | Example 2: 2,000 20mm equivalent greenfield development |  | Example 3: 10,000 20mm equivalent greenfield development
[5 empty] | Water | Sewerage | Water | Sewerage | Water | Sewerage
Scheme characteristics
|  |  |  | End use customers | 1,800 residential apartments; 200 20mm equivalent commercial properties | 1,800 residential apartments; 200 20mm equivalent commercial properties | 1,800 residential houses & 200 of commercial properties | 1,800 residential houses & 200 of commercial properties | 9,000 residential houses & 1,000 of commercial properties | 9,000 residential houses & 1,000 of commercial properties
|  |  |  | Water meters (connection point to incumbent) | 2 x 80mm 1 x 150 mm | 1x 150mm | 1x 20mm | 1x100mm | 1x20mm | 1x100mm
|  |  |  | Water consumption (from incumbent's network) | 262,800kL/year |  | 760,242kL/year |  | 3,547,800kL/year
|  |  |  | Sewage discharge (to incumbent's network |  | 210,240kL/year |  | 532,170kL/year |  | 2,483,460kL/year
Retail metering
|  |  |  | Number of meters | 2000 | 2000 | 2000 | 2000 | 10000 | 10000
|  |  |  | Capital expenditure | 1000000 |  | 1000000 |  | 5000000
Average asset lives
Retail metering Operating expenditure
Retail infrastructure
|  |  |  | Billing services | 96000 |  | 96000 |  | 240000
Quantity |  |  |  | Call centre services | 96000 |  | 96000 |  | 480000
|  |  |  | Outbound customer communications | 24000 |  | 24000 |  | 60000
|  |  |  | Other retail activities | 24000 |  | 24000 |  | 60000
|  |  |  | Retail Non-Meter Retail Operating Expenditure | 240000 |  | 240000 |  | 840000
Service Connection Length |  |  | 10
| Case 1 | Case 2 | Case 3
Rates | Qty | Qty |  | Reticulation network
64.17 |  | 20000 | 100000 | DN20 - Water Service Connection |  |  | 1283400 |  | 6417000
64.17 |  |  |  | DN50 uPVC - Water
82.8 | 640 |  |  | DN80 uPVC - Water | 52992
209.07 |  |  |  | DN100 DICL - Brownfield - Water
270.135 | 1100 |  |  | DN150 DICL - Brownfield - Water | 297148.5
342.585 |  |  |  | DN200 DICL - Brownfield - Water
405.72 | 1420 |  |  | DN250 DICL - Brownfield - Water | 576122.4
478.17 |  |  |  | DN300 DICL - Brownfield - Water
612.72 |  |  |  | DN375 DICL - Brownfield - Water
165.6 |  | 20400 | 95200 | DN100 DICL - Greenfield - Water |  |  | 3378240 |  | 15765120
207 |  |  |  | DN150 DICL - Greenfield - Water
258.75 |  |  |  | DN200 DICL - Greenfield - Water
300.15 |  | 13440 |  | DN250 DICL - Greenfield - Water |  |  | 4034016
351.9 |  |  |  | DN300 DICL - Greenfield - Water
445.05 |  |  |  | DN375 DICL - Greenfield - Water
527.85 |  |  | 8960 | DN450 DICL - Greenfield - Water |  |  |  |  | 4729536
267.03 |  |  |  | DN100 - Brownfield - Sewer
324.99 | 320 |  |  | DN150 - Brownfield - Sewer |  | 103996.8
431.595 | 1300 |  |  | DN225 - Brownfield - Sewer |  | 561073.5
568.215 |  |  |  | DN300 - Brownfield - Sewer
740.025 | 300 |  |  | DN375 - Brownfield - Sewer |  | 222007.5
903.555 |  |  |  | DN450 - Brownfield - Sewer
1041.21 |  |  |  | DN500 - Brownfield - Sewer
1315.485 |  |  |  | DN600 - Brownfield - Sewer
223.56 |  | 20000 | 100000 | DN100 - Greenfield - Sewer |  |  |  | 4471200 |  | 22356000
261.855 |  |  |  | DN150 - Greenfield - Sewer
326.025 |  | 28560 | 133280 | DN225 - Greenfield - Sewer |  |  |  | 9311274 |  | 43452612
441.945 |  |  |  | DN300 - Greenfield - Sewer
572.355 |  | 8040 | 17920 | DN375 - Greenfield - Sewer |  |  |  | 4601734.2 |  | 10256601.6
693.45 |  |  |  | DN450 - Greenfield - Sewer
802.125 |  |  |  | DN500 - Greenfield - Sewer
1035 |  |  | 17920 | DN600 - Greenfield - Sewer | [5 empty] | 18547200
119.025 |  |  |  | DN100 DICL - Sewer Pressure Pipe
119.025 |  |  |  | DN100 DICL - Sewer Pressure Pipe
165.6 |  |  |  | DN150 DICL - Sewer Pressure Pipe
196.65 |  | 1000 | 3000 | DN200 DICL - Sewer Pressure Pipe |  |  |  | 196650 |  | 589950
243.225 |  |  |  | DN250 DICL - Sewer Pressure Pipe
DN300 DICL - Sewer Pressure Pipe
DN375 DICL - Sewer Pressure Pipe
|  |  |  | Total length of reticulation network | 3160 | 1920 | 53840 | 57600 | 204160 | 272120
|  |  |  | Reticulation Capital expenditure | 926262.9 | 887077.8 | 8695656 | 18580858.2 | 26911656 | 95202363.6
|  |  |  | Average asset lives | Pipe: 100 yrs Ancillary: 30 yrs | 100 yrs | Pipe: 100 yrs Ancillary: 30 yrs | 100 yrs | Pipe: 100 yrs Ancillary: 30 yrs | 100 yrs
|  |  |  | Reticulation annual operating expenditure | 6320 | 5760 | 107680 | 172800 | 408320 | 816360
Distribution system pumping station (if typically necessary)
Sewerage Pump - 10L/s
434700 |  |  |  | Sewerage Pump - 20L/s
548550 |  |  |  | Sewerage Pump - 30L/s
652050 |  |  |  | Sewerage Pump - 40L/s
745200 |  |  |  | Sewerage Pump - 50L/s
828000 |  |  |  | Sewerage Pump - 60L/s
983250 |  | 1 | 3 | Sewerage Pump - 80L/s |  |  |  | 983250 |  | 2949750
1107450 |  |  |  | Sewerage Pump - 100L/s
1345500 |  |  |  | Sewerage Pump - 140L/s
1552500 |  |  |  | Sewerage Pump - 180L/s
1656000 |  |  |  | Sewerage Pump - 200L/s
2173500 |  | 1 | 2 | Water Service Reservoirs - 10ML |  |  | 2173500 |  | 4347000
382950 |  | 1 | 2 | Water Pumping Station - 100kW |  |  | 382950 |  | 765900
|  |  |  | Pumping capital expenditure |  |  | 2556450 | 983250 | 5112900 | 2949750
|  |  |  | Average asset lives |  |  | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 15-25 years | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 15-25 years
|  |  |  | Pumping annual operating expenditure |  |  | 46910 | 14490 | 153820 | 43470
|  |  |  | Total Capital Expenditures |  | 2813340.7 |  | 31816214.2 |  | 135176669.6
|  |  |  | Total Operating Expenditures |  | 252080 |  | 581880 |  | 2261970
|  |  |  | Capex per property |  | 1406.6704 |  | 15908.1071 |  | 13517.667
|  |  |  | Opex per property |  | 126.04 |  | 290.94 |  | 226.197
Note on F23: Tim Ryan: These costs are annual and for the provision of both water and wastewater

## Operating Cost Summary
OPERATING COST SUMMARY
Item | Cost | UoM | Remarks | Reference
Water main | 2 | per m
| 50 | '000 / 100km | Operation Cost | 2013-14 Water Supply and Sewerage NSW Benchmarking Report, Table 13
| 143 | '000 / 100km | Maintenance cost
Water Pump Station | 26910 | each
| 3 | '000 / Pump | Operation Cost
| 5 | '000 / Pump | Maintenance cost
| 18 | '000 / Pump | Energy Cost
Water Reservoir | 10 | per property
| 9 | per property
Sewer Main | 3 | per m
| 73 | '000 / 100km | Operation Cost | 2013-14 Water Supply and Sewerage NSW Benchmarking Report, Table 18
| 157 | '000 / 100km | Maintenance cost
Sewer Pump Station | 14490 | each
| 5 | '000 / Pump | Operation Cost
| 5 | '000 / Pump | Maintenance cost
| 4 | '000 / Pump | Energy Cost

## Scenario Assumptions
ASSUMPTIONS REGARDING EXAMPLE SCENARIO COSTINGS
Assumptions and Qualifications
Common to all scenarios
| 1- | This cost estimate was completed based on the following:
a- Brownfield development has lesser land size and requires med to high density zoning to accommodate the proposed development
b- Greenfield development has larger land size and will be low density zoning to accommodate the proposed development
| 2- | Service mains (i.e. from reticulation main to property connection) assumed to be 10m in length
Case 1 - Brownfield with 2,000 Equivalent
Common
| 1- | Quantity of pipework based on:
a- total development size of 300m x 260m
b- total 8 street block, each has 4x service connections
c- Block size at 100m x 50m with 10 level of residential and ground level for commercial (total 11 Levels)
d- road reserve width at 20m, total road length estimated to be 2200m
e- 50% build-up area per lot (i.e. half of the land area is building structure
| 2- | Assets' expected life and usage calculation based on WSA02 - Sewerage Code of Australia
| 3- | Rates allow for existing services and associated increased construction difficulties
| 4- | Both pipe size and length may varies pending on water consumption and sewage flow assumed and the layout of the development site.
Water Infrastructure
| 1- | Single DN250 feed pipe from authority main to development site
| 2- | No allowance for water booster pump station. i.e. There is sufficient pressure in the authority main to supply the whole development
| 3- | DN250 ring main allowed around the perimeter of development site to provide redundancy and security of supply in the event of shut down for maintenance
| 4- | Min DN150 for all water reticulation main to allow for firewater connection(s) of potable water reticulation network
| 5- | Based on one service connection point per apartment block (with 2x DN80 and 1x DN150 water service connections)
| 6- | Valves, hydrants and associated fittings are accounted for within the unit rates of pipework
Sewerage Infrastructure
| 1- | Single sewer discharge from development site to town main
| 2- | Based on one service connection point per apartment block (with 1x DN150 sewer connection)
| 3- | Manholes and bends are accounted for within the unit rates of pipework
| 4- | Authority receiving sewer has capacity floes from development via gravity
Case 2 - Greenfield with 2,000 Equivalent
Common
| 1- | Quantity of pipework based on:
a- total development size of 2km x 1km
b- total 36 street block, each has 20x service connections
c- block size at 200m x 50m with 500m2 land lot for property
d- road reserve width at 20m, total length estimated to be 39km
e- total 1,800 residential and 200 commercial properties
| 2- | Rates assumed no existing services
| 3- | Both pipe size and length may varies pending on water consumption and sewage flow assumed and the layout of the development site.
Water Infrastructure
| 1- | Single DN250 feed pipe from authority main to development site
| 2- | Total 1x water pumping stations and water reservoirs allowed for water supply to the whole development
| 3- | DN250 ring main allowed around the perimeter of development site to provide redundancy and security of supply in the event of shut down for maintenance
| 4- | Min DN100 for all water reticulation main to allow for firewater connection(s) of potable water reticulation network
| 5- | Based on one service connection point per property (with 1x DN20 water service connections)
| 6- | Valves, hydrants and associated fittings are accounted for within the unit rates of pipework
Sewerage Infrastructure
| 1- | Single sewer discharge from development site to town main
| 2- | Based on one service connection point per property (with 1x DN100 sewer connection)
| 3- | Manholes and bends are accounted for within the unit rates of pipework
| 4- | Due to topography and development size, 1x sewerage pumping station allowed.
| 5- | Assumed all property wastewater will be gravity drained to sewerage pumping station(s)
| 6- | Total 2x sewerage pumping stations allowed for sewerage discharge from the whole development to authority mains (assumed 2x sewerage discharge points)
Case 3 - Greenfield with 10,000 Equivalent
Common
| 1- | Quantity of pipework based on:
a- total development size of 3km x 3km
b- total 180 street block, each has 20x service connections
c- block size at 200m x 50m with 500m2 land lot for property
d- road reserve width at 20m, total length estimated to be 180km
e- total 9,000 residential and 1,000 commercial properties
| 2- | Rates assumed no existing services
| 3- | both pipe size and length may varies pending on water consumption and sewage flow assumed and the layout of the development site.
Water Infrastructure
| 1- | Single DN450 feed pipe from authority main to development site
| 2- | Total 2x water pumping stations and water reservoirs allowed for water supply to the whole development
| 3- | DN450 ring main allowed around the perimeter of development site to provide redundancy and security of supply in the event of shut down for maintenance
| 4- | Min DN100 for all water reticulation main to allow for firewater connection(s) of potable water reticulation network
| 5- | Based on one service connection point per property (with 1x DN20 water service connections)
| 6- | Valves, hydrants and associated fittings are accounted for within the unit rates of pipework
Sewerage Infrastructure
| 1- | Two sewer discharge from development site to town main
| 2- | Based on one service connection point per property (with 1x DN100 sewer connection)
| 3- | Manholes and bends are accounted for within the unit rates of pipework
| 4- | Due to topography and development size, 3x sewerage pumping station allowed.
| 5- | Assumed all property wastewater will be gravity drained to sewerage pumping station(s)
| 6- | Assumed wastewater to be gravity drained to two sewerage pumping stations prior to discharge to town sewer main via sewer rising main

## Scenario Layouts
ASSUMED LAYOUTS FOR EACH EXAMPLE SCENARIO
Case 1 - Brownfield with 2,000 Equivalent
Case 2 - Greenfield with 2,000 Equivalent
Case 3 - Greenfield with 10,000 Equivalent

## Name Ranges (hidden)
Service_Names
Water Retail
Water Reticulation
Wastewater Retail
Wastewater Reticulation - Gravity
Wastewater Reticulation - Pressure