## Cover Sheet
REVISED CALCULATION OF REASONABLY EFFICIENT COMPETITOR COSTS
DISCLAIMER:
The Excel Spreadsheet has been prepared for the Independent Pricing and Regulatory Tribunal as part of its review into wholesale water and sewerage prices. The analysis and information provided in this Excel Spreadsheet is derived in whole or in part from information prepared by a range of parties other than Oakley Greenwood. Oakley Greenwood explicitly disclaims liability for any errors or omissions in that information, or any other aspect of the validity of that information. We also disclaim liability for the use of any information in this report by any party for any purpose other than the intended purpose.
DESCRIPTION OF SPREADSHEET:
This Excel Spreadsheet provides our revised calculation of reasonably efficient competitor costs based on responses to our report "Calculation of Reasonably Efficient Competitor Costs" which was publicly released with the Independent Pricing and Regulatory Tribunal's Draft Report and Draft Determinations. This Excel Spreadsheet sets out benchmark unit rates for a reasonably efficient competitor seeking to enter the water and/or sewerage industries. We have sought to indicate whether certain factors would influence the costs of each of the asset categories and then used these benchmark unit rates in a number of examples scenarios to demonstrate the likely cost to be faced by a new entrant seeking to provide water and/or sewerage services. The assumptions that we have used to cost the example scenarios are contained in the tabs following Example Scenario. Annual estimates of operating costs for different assets based on assumed lifycle profiles has also been developed and incorporated within this spreadsheet. The associated reports for this spreadsheet are "Revised Calculation of Reasonably Efficient Competitor Costs Report" and "Calculation of Reasonably Efficient Competitor Costs".

## Scenario Assumptions
ASSUMPTIONS REGARDING EXAMPLE SCENARIO COSTINGS
Assumptions and Qualifications
Common to all scenarios
| 1- | This cost estimate was completed based on the following:
a- Brownfield development has lesser land size and requires med to high density zoning to accommodate the proposed development
b- Greenfield development has larger land size and will be low density zoning to accommodate the proposed development
| 2- | Service mains (i.e. from reticulation main to property connection) assumed to be 10m in length
Case 1 - Brownfield with 2,000 Equivalent
Common
| 1- | Quantity of pipework based on:
a- total development size of 300m x 260m
b- total 8 street block, each has 4x service connections
c- Block size at 100m x 50m with 10 level of residential and ground level for commercial (total 11 Levels)
d- road reserve width at 20m, total road length estimated to be 2200m
e- 50% build-up area per lot (i.e. half of the land area is building structure
| 2- | Assets' expected life and usage calculation based on WSA02 - Sewerage Code of Australia
| 3- | Rates allow for existing services and associated increased construction difficulties
| 4- | Both pipe size and length may varies pending on water consumption and sewage flow assumed and the layout of the development site.
Water Infrastructure
| 1- | Single DN250 feed pipe from authority main to development site
| 2- | No allowance for water booster pump station. i.e. There is sufficient pressure in the authority main to supply the whole development
| 3- | DN250 ring main allowed around the perimeter of development site to provide redundancy and security of supply in the event of shut down for maintenance
| 4- | Min DN150 for all water reticulation main to allow for firewater connection(s) of potable water reticulation network
| 5- | Based on one service connection point per apartment block (with 2x DN80 and 1x DN150 water service connections)
| 6- | Valves, hydrants and associated fittings are accounted for within the unit rates of pipework
Sewerage Infrastructure
| 1- | Single sewer discharge from development site to town main
| 2- | Based on one service connection point per apartment block (with 1x DN150 sewer connection)
| 3- | Manholes and bends are accounted for within the unit rates of pipework
| 4- | Authority receiving sewer has capacity floes from development via gravity
Case 2 - Greenfield with 2,000 Equivalent
Common
| 1- | Quantity of pipework based on:
a- total development size of 2km x 1km
b- total 36 street block, each has 20x service connections
c- block size at 200m x 50m with 500m2 land lot for property
d- road reserve width at 20m, total length estimated to be 39km
e- total 1,800 residential and 200 commercial properties
| 2- | Rates assumed no existing services
| 3- | Both pipe size and length may varies pending on water consumption and sewage flow assumed and the layout of the development site.
Water Infrastructure
| 1- | Single DN250 feed pipe from authority main to development site
| 2- | Total 1x water pumping stations and water reservoirs allowed for water supply to the whole development
| 3- | DN250 ring main allowed around the perimeter of development site to provide redundancy and security of supply in the event of shut down for maintenance
| 4- | Min DN100 for all water reticulation main to allow for firewater connection(s) of potable water reticulation network
| 5- | Based on one service connection point per property (with 1x DN20 water service connections)
| 6- | Valves, hydrants and associated fittings are accounted for within the unit rates of pipework
Sewerage Infrastructure
| 1- | Single sewer discharge from development site to town main
| 2- | Based on one service connection point per property (with 1x DN100 sewer connection)
| 3- | Manholes and bends are accounted for within the unit rates of pipework
| 4- | Due to topography and development size, 1x sewerage pumping station allowed.
| 5- | Assumed all property wastewater will be gravity drained to sewerage pumping station(s)
| 6- | Total 2x sewerage pumping stations allowed for sewerage discharge from the whole development to authority mains (assumed 2x sewerage discharge points)
Case 3 - Greenfield with 10,000 Equivalent
Common
| 1- | Quantity of pipework based on:
a- total development size of 3km x 3km
b- total 180 street block, each has 20x service connections
c- block size at 200m x 50m with 500m2 land lot for property
d- road reserve width at 20m, total length estimated to be 180km
e- total 9,000 residential and 1,000 commercial properties
| 2- | Rates assumed no existing services
| 3- | both pipe size and length may varies pending on water consumption and sewage flow assumed and the layout of the development site.
Water Infrastructure
| 1- | Single DN450 feed pipe from authority main to development site
| 2- | Total 2x water pumping stations and water reservoirs allowed for water supply to the whole development
| 3- | DN450 ring main allowed around the perimeter of development site to provide redundancy and security of supply in the event of shut down for maintenance
| 4- | Min DN100 for all water reticulation main to allow for firewater connection(s) of potable water reticulation network
| 5- | Based on one service connection point per property (with 1x DN20 water service connections)
| 6- | Valves, hydrants and associated fittings are accounted for within the unit rates of pipework
Sewerage Infrastructure
| 1- | Two sewer discharge from development site to town main
| 2- | Based on one service connection point per property (with 1x DN100 sewer connection)
| 3- | Manholes and bends are accounted for within the unit rates of pipework
| 4- | Due to topography and development size, 3x sewerage pumping station allowed.
| 5- | Assumed all property wastewater will be gravity drained to sewerage pumping station(s)
| 6- | Assumed wastewater to be gravity drained to two sewerage pumping stations prior to discharge to town sewer main via sewer rising main

## Scenario Layouts
ASSUMED LAYOUTS FOR EACH EXAMPLE SCENARIO
Case 1 - Brownfield with 2,000 Equivalent
Case 2 - Greenfield with 2,000 Equivalent
Case 3 - Greenfield with 10,000 Equivalent

## Benchmark Unit Rates
Inflation Factor
1.031
BENCHMARK UNIT RATES
|  | Service | Asset | Standardised Unit | Asset Characteristics |  |  | Factors that Influence Characteristics |  |  |  |  | Comments
[5 empty] | Value per Unit | Expected Life | Lifecycle Opex | Economies of Scale | Economies of Scope | Topography | Geotechnical | Delivery of Service
| FOR EXAMPLE | Water Retail | 20mm meter - Remote Unit | Each | 450 | 12 years | Nil. To be managed by property owner | The density and the size of development is unlikely to have an impact on the unit cost. | As the water meter is generally required to be installed by licenced plumbers, thus it is unlikely to have an impact on the unit cost | The topography is unlikely to have an impact on the unit cost of 20mm meters | The geotechnical condition of the ground is unlikely to have an impact on the unit cost as it is likely to be installed above ground | Different delivery options may impact on factors such as warehousing costs, however it is unlikely to be a material impact on this high level analysis. | Based on $200 for a remote unit and $250 for installation cost
|  | Water Retail | 20mm meter - Standard Unit | Each | 320 | 12 years | See Above | See Above | See Above | See Above | See Above | See Above | Based on $70 for a remote unit and $250 for installation cost
|  | Water Retail | Billing Services | Per customer, per month | $2-$4 | NA | Only Opex | The range provided is based on the number of customers that would be serviced by the new entrant. The lower end of the range ($2) would represent a higher customer base, while the upper end of the range ($4) would represent a smaller customer base. | There would be economies of scope for billing services - as costs for providing billing services for water-only, wastewater-only or a combined water and wastewater service would be the same (assuming the same number of customers). | No impact on the unit rate of this service | No impact on the unit rate of this service | Given upfront costs of establishing these retail services, we have assumed that these services would be more efficiently provided through an external service provider | Based on information provided by external managed service provider.
|  | Water Retail | Call Centre Services | Per customer, per annum | 15.45 | NA | Only Opex | There are unlikely to be material differences in the unit rates for the size of customers for call centre services. However there is likely to be differences in the unit rates for different scale of the REC (discussed in delivery section). | There are economies of scope in call centre costs for providing wastewater services in addition to water services as the additional call centre costs for wastewater services would be expected to be lower. | No impact on the unit rate of this service | No impact on the unit rate of this service | Delivery has been separated depending on the size of the development. We have assumed that the smaller example schemes will maintain the call centre within the management staff resources, however the larger example scheme will require a more complex solution and would therefore outsource the service. | Based on quoted information from an outsourcing call centre that has previously provided services to the electricity industry.
|  | Water Retail | Meter Reading | Per meter, per annum | 2.5 | NA | Only Opex | The density of the meters is likely to impact on the cost to the service provider. For this reason we have considered that manual meter reading would be undertaken for brownfield developments (based on higher density) and remotely read meters for greenfield developments (therefore no meter reading costs factored in through this process) | There may be economies of scope where a new entrant is already purchasing meter reading services for electricity and/or gas. | No impact on the unit rate of this service | No impact on the unit rate of this service | Given upfront costs of establishing these retail services, we have assumed that these services would be more efficiently provided through an external service provider | Based on information provided by the industry regarding previous meter reading quotes and public information.
|  | Water Retail | Outbound Customer Communications | Per customer, per month | $0.50-$1 | NA | Only Opex | The range provided is based on the number of customers that would be serviced by the new entrant. The lower end of the range ($0.50) would represent a higher customer base, while the upper end of the range ($1) would represent a smaller customer base. | No impact on the unit rate of this service | No impact on the unit rate of this service | No impact on the unit rate of this service | Given upfront costs of establishing these retail services, we have assumed that these services would be more efficiently provided through an external service provider | Based on information provided by external managed service provider.
|  | Water Retail | Other Retail Services | Per customer, per month | $0.50-$1 | NA | Only Opex | The range provided is based on the number of customers that would be serviced by the new entrant. The lower end of the range ($0.50) would represent a higher customer base, while the upper end of the range ($1) would represent a smaller customer base. | No impact on the unit rate of this service | No impact on the unit rate of this service | No impact on the unit rate of this service | Given upfront costs of establishing these retail services, we have assumed that these services would be more efficiently provided through an external service provider | Based on information provided by external managed service provider and industry knowledge.
|  | Wastewater Retail | Boundary Traps | Each | 1000 |  | Nil. To be managed by property owner | Nil assumed to be installed / constructed by property developer | Nil assumed to be installed / constructed by property developer | Nil assumed to be installed / constructed by property developer | Nil assumed to be installed / constructed by property developer |  | Assumed
|  | Wastewater Retail | DN20 - Water Service Connection | Metre | 63.922 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | The density and the size of development is unlikely to have an impact on the unit cost. | As the water service connection is generally required to be installed by licenced plumbers, thus it is unlikely to have an impact on the unit cost | The topography is unlikely to have an impact as the average depth of pipe is similar in flat and undulated terrains. | Ground condition such as rock excavation, contaminated soil, water charged ground and bearing capacity is likely to have an impact on the unit cost. Encountering rock in trench installation can increase the cost by 20% to 5 times pending on the strength and level of the rock in the pipe trench. |  | Asset life based on Water Supply Code of Australia Unit rate based on DN50 uPVC - Water pipe Opex based on "2013-14 Water Supply and Sewerage NSW Benchmarking Report" Benchmarking cost data, published by Department of Primary Industries, increased to 2016 prices with CPI of 3.1%
|  | Water Reticulation | DN50 uPVC - Water | Metre | 63.922 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | The density and the size of development is unlikely to have an impact on the unit cost. | Capex cost may be lower if utility services (such as water, sewer, stormwater) can be installed by a single civil contractor. | The topography is unlikely to have an impact on the unit cost as the average depth of pipe is similar in flat and undulated terrains. | Ground condition such as rock excavation, contaminated soil, water charged ground and bearing capacity is likely to have an impact on the unit cost. Encountering rock in trench installation can increase the cost by 20% to 5 times pending on the strength and level of the rock in the pipe trench. |  | Asset life based on Water Supply Code of Australia Rates are based on "NSW Reference Rates Manual - Valuation of water supply, sewerage and stormwater assets", published by Department of Primary Industries - Office of Water, 2014, increased to 2016 prices with CPI of 3.1% Opex based on "2013-14 Water Supply and Sewerage NSW Benchmarking Report" Benchmarking cost data, published by Department of Primary Industries, increased to 2016 prices with CPI of 3.1%
|  | Water Reticulation | DN80 uPVC - Water | Metre | 82.48 | Pipe: 100 years Valves: 30 years | $2 / metre | Denser development may assist with reducing the length of pipe required, however, it may require larger pipe size which has a higher unit cost | Capex cost may be lower if utility services (such as water, sewer, stormwater) can be installed by a single civil contractor. | The topography is unlikely to have an impact on the unit cost as the average depth of pipe is similar in flat and undulated terrains. | Ground condition such as rock excavation, contaminated soil, water charged ground and bearing capacity is likely to have an impact on the unit cost. Encountering rock in trench installation can increase the cost by 20% to 5 times pending on the strength and level of the rock in the pipe trench. |  | Asset life based on Water Supply Code of Australia For water reticulation networks, the typical spacing for valves is around 200m, depending on the complexity of the system. Based on this, it is estimated that approximately 5-20% of pipe-related capex is related to valves. Rates are based on "NSW Reference Rates Manual - Valuation of water supply, sewerage and stormwater assets", published by Department of Primary Industries - Office of Water, 2014, increased to 2016 price with CPI of 3.5% Opex based on "2013-14 Water Supply and Sewerage NSW Benchmarking Report" Benchmarking cost data, published by Department of Primary Industries, increased to 2016 prices with CPI of 3.5%
|  | Water Reticulation | DN50 uPVC - Brownfield - Water | Metre | 107.224 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | Denser development may assist with reducing the length of pipe required, however, it may require larger pipe size which has a higher unit cost | Capex cost may be lower if utility services (such as water, sewer, stormwater) can be installed by a single civil contractor. | The topography is unlikely to have an impact on the unit cost as the average depth of pipe is similar in flat and undulated terrains. | Ground condition such as rock excavation, contaminated soil, water charged ground and bearing capacity is likely to have an impact on the unit cost. Encountering rock in trench installation can increase the cost by 20% to 5 times pending on the strength and level of the rock in the pipe trench. |  | Asset life based on Water Supply Code of Australia Unit rate based on minimum pipe installation depth as per Water Supply Code of Australia (typical 600-750mm, laid in roadway). Rates are based on "NSW Reference Rates Manual - Valuation of water supply, sewerage and stormwater assets", published by Department of Primary Industries - Office of Water, 2014, increased to 2016 prices with CPI of 3.1% For brownfield installation, additional cost of moderate construction difficulty has been applied (e.g. existing services) Opex based on "2013-14 Water Supply and Sewerage NSW Benchmarking Report" Benchmarking cost data, published by Department of Primary Industries, increased to 2016 prices with CPI of 3.1%
|  | Water Reticulation | DN80 uPVC - Brownfield - Water | Metre | 125.782 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN100 uPVC - Brownfield - Water | Metre | 141.247 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN150 uPVC - Brownfield - Water | Metre | 207.231 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN200 uPVC - Brownfield - Water | Metre | 279.401 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN250 uPVC - Brownfield - Water | Metre | 362.912 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN300 uPVC - Brownfield - Water | Metre | 455.702 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN375 uPVC - Brownfield - Water | Metre | 600.042 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN50 uPVC - Greenfield - Water | Metre | 51.55 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | Denser development may assist with reducing the length of pipe required, however, it may require larger pipe size which has a higher unit cost | Capex cost may be lower if utility services (such as water, sewer, stormwater) can be installed by a single civil contractor. | The topography is unlikely to have an impact on the unit cost as the average depth of pipe is similar in flat and undulated terrains. | Ground condition such as rock excavation, contaminated soil, water charged ground and bearing capacity is likely to have an impact on the unit cost. Encountering rock in trench installation can increase the cost by 20% to 5 times pending on the strength and level of the rock in the pipe trench. |  | Asset life based on Water Supply Code of Australia 'Unit rate based on minimum pipe installation depth as per Water Supply Code of Australia (typical 600-750mm, laid in roadway). Rates are based on "NSW Reference Rates Manual - Valuation of water supply, sewerage and stormwater assets", published by Department of Primary Industries - Office of Water, 2014, increased to 2016 prices with CPI of 3.1% Opex based on "2013-14 Water Supply and Sewerage NSW Benchmarking Report" Benchmarking cost data, published by Department of Primary Industries, increased to 2016 prices with CPI of 3.1%
|  | Water Reticulation | DN80 uPVC - Greenfield - Water | Metre | 70.108 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN100 uPVC - Greenfield - Water | Metre | 85.573 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN150 uPVC - Greenfield - Water | Metre | 131.968 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN200 uPVC - Greenfield - Water | Metre | 183.518 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN250 uPVC - Greenfield - Water | Metre | 245.378 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN300 uPVC - Greenfield - Water | Metre | 317.548 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN375 uPVC - Greenfield - Water | Metre | 420.648 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | See above | See above | See above | See above |  | See above
CPI | 1.031 | Water Reticulation | DN100 DICL - Brownfield - Water | Metre | 208.262 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | Denser development may assist with reducing the length of pipe required, however, it may require larger pipe size which has a higher unit cost | Capex cost may be lower if utility services (such as water, sewer, stormwater) can be installed by a single civil contractor. | The topography is unlikely to have an impact on the unit cost as the average depth of pipe is similar in flat and undulated terrains. | Ground condition such as rock excavation, contaminated soil, water charged ground and bearing capacity is likely to have an impact on the unit cost. Encountering rock in trench installation can increase the cost by 20% to 5 times pending on the strength and level of the rock in the pipe trench. |  | Asset life based on Water Supply Code of Australia 'Unit rate based on minimum pipe installation depth as per Water Supply Code of Australia (typical 600-750mm, laid in roadway). Rates are based on "NSW Reference Rates Manual - Valuation of water supply, sewerage and stormwater assets", published by Department of Primary Industries - Office of Water, 2014, increased to 2016 prices with CPI of 3.1% For brownfield installation, additional cost of moderate construction difficulty has been applied (e.g. existing services) Opex based on "2013-14 Water Supply and Sewerage NSW Benchmarking Report" Benchmarking cost data, published by Department of Primary Industries, increased to 2016 prices with CPI of 3.1%
|  | Water Reticulation | DN150 DICL - Brownfield - Water | Metre | 269.091 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN200 DICL - Brownfield - Water | Metre | 341.261 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN250 DICL - Brownfield - Water | Metre | 404.152 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN300 DICL - Brownfield - Water | Metre | 476.322 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN375 DICL - Brownfield - Water | Metre | 610.352 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN100 DICL - Greenfield - Water | Metre | 152.588 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | Denser development may assist with reducing the length of pipe required, however, it may require larger pipe size which has a higher unit cost | Capex cost may be lower if utility services (such as water, sewer, stormwater) can be installed by a single civil contractor. | The topography is unlikely to have an impact on the unit cost as the average depth of pipe is similar in flat and undulated terrains. | Ground condition such as rock excavation, contaminated soil, water charged ground and bearing capacity is likely to have an impact on the unit cost. Encountering rock in trench installation can increase the cost by 20% to 5 times pending on the strength and level of the rock in the pipe trench. |  | Asset life based on Water Supply Code of Australia 'Unit rate based on minimum pipe installation depth as per Water Supply Code of Australia (typical 600-750mm, laid in roadway). Rates are based on "NSW Reference Rates Manual - Valuation of water supply, sewerage and stormwater assets", published by Department of Primary Industries - Office of Water, 2014, increased to 2016 prices with CPI of 3.1% Opex based on "2013-14 Water Supply and Sewerage NSW Benchmarking Report" Benchmarking cost data, published by Department of Primary Industries, increased to 2016 prices with CPI of 3.1%
|  | Water Reticulation | DN150 DICL - Greenfield - Water | Metre | 193.828 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN200 DICL - Greenfield - Water | Metre | 245.378 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN250 DICL - Greenfield - Water | Metre | 286.618 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN300 DICL - Greenfield - Water | Metre | 338.168 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN375 DICL - Greenfield - Water | Metre | 430.958 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Water Reticulation | DN450 DICL - Greenfield - Water | Metre | 513.438 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $1.99/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN100 - Brownfield - Sewer | Metre | 265.998 | Pipe: 100 years Maint Struct: 100 years | $0.76/m (New asset) $2.37/m (100yr avg) | Denser development may assist with reducing the length of pipe required, however, it may require larger pipe size which has a higher unit cost | Capex cost may be lower if utility services (such as water, sewer, stormwater) can be installed by a single civil contractor. | The topography is likely to have an impact on the unit cost as the sewer gravity main would have a deeper average depth in flatter terrain compared to undulating terrain. Pending on the installation depth of the sewer gravity main, the unit cost could double to 3 times for a depth up to 4.5m | Ground condition such as rock excavation, contaminated soil, water charged ground and bearing capacity is likely to have an impact on the unit cost. Encountering rock in trench installation can increase the cost by 20% to 5 times pending on the strength and level of the rock in the pipe trench. |  | Asset life based on Sewerage Code of Australia 'Unit rate based on minimum pipe installation depth as per Sewerage Code of Australia (typical 1.5m to 3.0m, laid in roadway). Rates are based on "NSW Reference Rates Manual - Valuation of water supply, sewerage and stormwater assets", published by Department of Primary Industries - Office of Water, 2014, increased to 2016 prices with CPI of 3.1% For brownfield installation, additional cost of moderate construction difficulty has been applied (e.g. existing services) Opex based on "2013-14 Water Supply and Sewerage NSW Benchmarking Report" Benchmarking cost data, published by Department of Primary Industries, increased to 2016 prices with CPI of 3.1%
|  | Wastewater Reticulation - Gravity | DN150 - Brownfield - Sewer | Metre | 323.734 | Pipe: 100 years Maint Struct: 100 years | $0.76/m (New asset) $2.37/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN225 - Brownfield - Sewer | Metre | 429.927 | Pipe: 100 years Maint Struct: 100 years | $0.76/m (New asset) $2.37/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN300 - Brownfield - Sewer | Metre | 566.019 | Pipe: 100 years Maint Struct: 100 years | $0.76/m (New asset) $2.37/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN375 - Brownfield - Sewer | Metre | 737.165 | Pipe: 100 years Maint Struct: 100 years | $0.76/m (New asset) $2.37/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN450 - Brownfield - Sewer | Metre | 900.063 | Pipe: 100 years Maint Struct: 100 years | $0.76/m (New asset) $2.37/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN500 - Brownfield - Sewer | Metre | 1037.186 | Pipe: 100 years Maint Struct: 100 years | $0.76/m (New asset) $2.37/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN600 - Brownfield - Sewer | Metre | 1310.401 | Pipe: 100 years Maint Struct: 100 years | $0.76/m (New asset) $2.37/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN100 - Greenfield - Sewer | Metre | 210.324 | Pipe: 100 years Maint Struct: 100 years | $0.76/m (New asset) $2.37/m (100yr avg) | Denser development may assist with reducing the length of pipe required, however, it may require larger pipe size which has a higher unit cost | Capex cost may be lower if utility services (such as water, sewer, stormwater) can be installed by a single civil contractor. | The topography is likely to have an impact on the unit cost as cost of installation increases with the deep of installation. The sewer gravity main would have a deeper average depth in flatter terrain compare to an undulated terrain. Pending on the installation depth of the sewer gravity main, the unit cost could double to 3 times for a depth up to 4.5m | Ground condition such as rock excavation, contaminated soil, water charged ground and bearing capacity is likely to have an impact on the unit cost. Encountering rock in trench installation can increase the cost by 20% to 5 times pending on the strength and level of the rock in the pipe trench. |  | Asset life based on Sewerage Code of Australia Unit rate based on minimum pipe installation depth as per Sewerage Code of Australia (typical 1.5m to 3.0m, laid in roadway). Rates are based on "NSW Reference Rates Manual - Valuation of water supply, sewerage and stormwater assets", published by Department of Primary Industries - Office of Water, 2014, increased to 2016 prices with CPI of 3.1% Opex based on "2013-14 Water Supply and Sewerage NSW Benchmarking Report", published by Department of Primary Industries, increased to 2016 prices with CPI of 3.1%
|  | Wastewater Reticulation - Gravity | DN150 - Greenfield - Sewer | Metre | 248.471 | Pipe: 100 years Maint Struct: 100 years | $0.76/m (New asset) $2.37/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN225 - Greenfield - Sewer | Metre | 312.393 | Pipe: 100 years Maint Struct: 100 years | $0.76/m (New asset) $2.37/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN300 - Greenfield - Sewer | Metre | 427.865 | Pipe: 100 years Maint Struct: 100 years | $0.76/m (New asset) $2.37/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN375 - Greenfield - Sewer | Metre | 557.771 | Pipe: 100 years Maint Struct: 100 years | $0.76/m (New asset) $2.37/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN450 - Greenfield - Sewer | Metre | 678.398 | Pipe: 100 years Maint Struct: 100 years | $0.76/m (New asset) $2.37/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN500 - Greenfield - Sewer | Metre | 786.653 | Pipe: 100 years Maint Struct: 100 years | $0.76/m (New asset) $2.37/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Gravity | DN600 - Greenfield - Sewer | Metre | 1018.628 | Pipe: 100 years Maint Struct: 100 years | $0.76/m (New asset) $2.37/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | DN100 DICL - Sewer Pressure Pipe | Metre | 106.193 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $2.13/m (100yr avg) | Denser development may assist with reducing the length of pipe required, however, it may require larger pipe size which has a higher unit cost | Capex cost may be lower if utility services (such as water, sewer, stormwater) can be installed by a single civil contractor. | The topography is unlikely to have an impact on the unit cost as the average depth of pipe is similar in flat and undulated terrains. | Ground condition such as rock excavation, contaminated soil, water charged ground and bearing capacity is likely to have an impact on the unit cost. Encountering rock in trench installation can increase the cost by 20% to 5 times pending on the strength and level of the rock in the pipe trench. |  | Asset life based on Sewerage Code of Australia 'Unit rate based on minimum pipe installation depth as per Sewerage Code of Australia (typical 600-750mm, laid in roadway). Rates are based on "NSW Reference Rates Manual - Valuation of water supply, sewerage and stormwater assets", published by Department of Primary Industries - Office of Water, 2014, increased to 2016 prices with CPI of 3.1% Opex based on "2013-14 Water Supply and Sewerage NSW Benchmarking Report", published by Department of Primary Industries, increased to 2016 prices with CPI of 3.1%
|  | Wastewater Reticulation - Pressure | DN150 DICL - Sewer Pressure Pipe | Metre | 152.588 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $2.13/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | DN200 DICL - Sewer Pressure Pipe | Metre | 183.518 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $2.13/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | DN250 DICL - Sewer Pressure Pipe | Metre | 229.913 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $2.13/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | DN300 DICL - Sewer Pressure Pipe | Metre | 291.773 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $2.13/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | DN375 DICL - Sewer Pressure Pipe | Metre | 400.028 | Pipe: 100 years Valves: 30 years | $0.52/m (New asset) $2.13/m (100yr avg) | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | Sewerage Pump - 10L/s | Each | 329920 | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 15-25 years | $14,490 / each | Unlikely to have an impact on the unit cost as the sizing of the pump station is independent of the denser | Capex cost may be lower if sewerage pumping station and unity services can be constructed together. Other factor such as sourcing off-the-shelf pump skid may also reduce the Capex Cost | The topography is unlikely to have an impact on the unit cost. | On the basis that, the sewer pump station is a wet well (typically 5m-10m deep), the ground condition such as rock excavation, contaminated soil, water charged ground and bearing capacity is likely to have an impact on the unit cost. |  | Asset life based on Sewage Pumping Station Code of Australia Rates are based on "NSW Reference Rates Manual - Valuation of water supply, sewerage and stormwater assets", published by Department of Primary Industries - Office of Water, 2014, increased to 2016 prices with CPI of 3.1% Opex based on "2013-14 Water Supply and Sewerage NSW Benchmarking Report" Benchmarking cost data, published by Department of Primary Industries, increased to 2016 prices with CPI of 3.1%
|  | Wastewater Reticulation - Pressure | Sewerage Pump - 20L/s | Each | 433020 | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 15-25 years | $14,490 / each | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | Sewerage Pump - 30L/s | Each | 546430 | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 15-25 years | $14,490 / each | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | Sewerage Pump - 40L/s | Each | 649530 | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 15-25 years | $14,490 / each | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | Sewerage Pump - 50L/s | Each | 742320 | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 15-25 years | $14,490 / each | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | Sewerage Pump - 60L/s | Each | 824800 | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 15-25 years | $14,490 / each | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | Sewerage Pump - 80L/s | Each | 979450 | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 15-25 years | $14,490 / each | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | Sewerage Pump - 100L/s | Each | 1103170 | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 15-25 years | $14,490 / each | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | Sewerage Pump - 140L/s | Each | 1340300 | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 15-25 years | $14,490 / each | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | Sewerage Pump - 180L/s | Each | 1546500 | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 15-25 years | $14,490 / each | See above | See above | See above | See above |  | See above
|  | Wastewater Reticulation - Pressure | Sewerage Pump - 200L/s | Each | 1649600 | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 15-25 years | $14,490 / each | See above | See above | See above | See above |  | See above
|  | Water Reticulation | Water Pumping Station - 10kW | Each | 82480 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $26,910 / each | Unlikely to have an impact on the unit cost as the sizing of the pump station is independent of the denser | Capex cost may be lower if water pumping station and water reservoir can be constructed together. Other factor such as sourcing off-the-shelf pump skid may also reduce the Capex Cost | On the basis that, the pumping station is an above ground structure, the topography is unlikely to have an impact on the unit cost. | On the basis that, the pumping station is above ground, the ground condition such as rock excavation, contaminated soil, water charged ground and bearing capacity is likely to have an impact on the unit cost. |  | Asset life based on Water Supply Code of Australia Rates are based on "NSW Reference Rates Manual - Valuation of water supply, sewerage and stormwater assets", published by Department of Primary Industries - Office of Water, 2014, increased to 2016 prices with CPI of 3.1% Opex based on "2013-14 Water Supply and Sewerage NSW Benchmarking Report" Benchmarking cost data, published by Department of Primary Industries, increased to 2016 prices with CPI of 3.1%
|  | Water Reticulation | Water Pumping Station - 20kW | Each | 118565 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $26,910 / each | See above | See above | See above | See above |  | See above
|  | Water Reticulation | Water Pumping Station - 30kW | Each | 144340 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $26,910 / each | See above | See above | See above | See above |  | See above
|  | Water Reticulation | Water Pumping Station - 50kW | Each | 195890 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $26,910 / each | See above | See above | See above | See above |  | See above
|  | Water Reticulation | Water Pumping Station - 100kW | Each | 381470 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $26,910 / each | See above | See above | See above | See above |  | See above
|  | Water Reticulation | Water Service Reservoirs - 0.5ML | Each | 407245 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $10 / property | Unlikely to have an impact on the unit cost as the sizing of the pump station is independent of the denser | Capex cost may be lower if water reservoir and water pumping station can be constructed together. | On the basis that, the reservoir is an above ground structure, the topography is unlikely to have an impact on the unit cost. | On the basis that, the reservoir is above ground, the ground condition such as rock excavation, contaminated soil, water charged ground and bearing capacity is likely to have an impact on the unit cost. |  | Asset life based on Water Supply Code of Australia Rates are based on "NSW Reference Rates Manual - Valuation of water supply, sewerage and stormwater assets", published by Department of Primary Industries - Office of Water, 2014, increased to 2016 prices with CPI of 3.1% Opex based on "2013-14 Water Supply and Sewerage NSW Benchmarking Report" Benchmarking cost data, published by Department of Primary Industries, increased to 2016 prices with CPI of 3.1%
|  | Water Reticulation | Water Service Reservoirs - 1ML | Each | 608290 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $10 / property | See above | See above | See above | See above |  | See above
|  | Water Reticulation | Water Service Reservoirs - 2ML | Each | 866040 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $10 / property | See above | See above | See above | See above |  | See above
|  | Water Reticulation | Water Service Reservoirs - 4ML | Each | 1185650 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $10 / property | See above | See above | See above | See above |  | See above
|  | Water Reticulation | Water Service Reservoirs - 5ML | Each | 1360920 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $10 / property | See above | See above | See above | See above |  | See above
|  | Water Reticulation | Water Service Reservoirs - 8ML | Each | 1855800 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $10 / property | See above | See above | See above | See above |  | See above
|  | Water Reticulation | Water Service Reservoirs - 10ML | Each | 2165100 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $10 / property | See above | See above | See above | See above |  | See above
|  | Water Reticulation | Water Service Reservoirs - 15ML | Each | 2938350 | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years | $10 / property | See above | See above | See above | See above |  | See above

## Example Scenarios
EXAMPLE SCENARIO COST INFORMATION
[5 empty] | Example 1: 2,000 20mm equivalent brownfield development |  | Example 2: 2,000 20mm equivalent greenfield development |  | Example 3: 10,000 20mm equivalent greenfield development
[5 empty] | Water | Sewerage | Water | Sewerage | Water | Sewerage
Scheme characteristics
|  |  |  | End use customers | 1,800 residential apartments; 200 20mm equivalent commercial properties | 1,800 residential apartments; 200 20mm equivalent commercial properties | 1,800 residential houses & 200 of commercial properties | 1,800 residential houses & 200 of commercial properties | 9,000 residential houses & 1,000 of commercial properties | 9,000 residential houses & 1,000 of commercial properties
|  |  |  | Water meters (connection point to incumbent) | 2 x 80mm 1 x 150 mm | 1x 150mm | 1x 20mm | 1x100mm | 1x20mm | 1x100mm
|  |  |  | Water consumption (from incumbent's network) | 262,800kL/year |  | 760,242kL/year |  | 3,547,800kL/year
|  |  |  | Sewage discharge (to incumbent's network |  | 210,240kL/year |  | 532,170kL/year |  | 2,483,460kL/year
Retail metering
|  |  |  | Number of meters | 2000 | 2000 | 2000 | 2000 | 10000 | 10000
|  |  |  | Capital expenditure - Remote Unit |  |  | 900000 |  | 4500000
|  |  |  | Capital expenditure - Standard Unit | 640000
Non-meter retail costs
|  |  |  | Billing services | 96000 |  | 96000 |  | 240000
|  |  |  | Call centre services - upfront | 1900 |  | 1900 |  | 11914
Quantity |  |  |  | Call centre services - ongoing | 0 |  | 0 |  | 154500
|  |  |  | Outbound customer communications | 24000 |  | 24000 |  | 60000
|  |  |  | Meter reading costs | 5000 |  | 0 |  | 0
|  |  |  | Management costs | 207423.2 |  | 207423.2 |  | 311134.8
|  |  |  | Other retail activities | 24000 |  | 24000 |  | 60000
|  |  |  | Retail Non-Meter Retail Operating Expenditure - Initial | 358323.2 |  | 353323.2 |  | 837548.8
|  |  |  | Retail Non-Meter Retail Operating Expenditure - Ongoing | 356423.2 |  | 351423.2 |  | 825634.8
Service Connection Length |  |  | 10
| Case 1 | Case 2 | Case 3
Rates | Qty | Qty |  | Reticulation network
63.922 |  | 20000 | 100000 | DN20 - Water Service Connection |  |  | 1278440 |  | 6392200
63.922 |  |  |  | DN50 uPVC - Water
82.48 | 640 |  |  | DN80 uPVC - Water | 52787.2
141.247 |  |  |  | DN100 uPVC - Brownfield - Water
207.231 | 1100 |  |  | DN150 uPVC - Brownfield - Water | 227954.1
279.401 |  |  |  | DN200 uPVC - Brownfield - Water
362.912 | 1420 |  |  | DN250 uPVC - Brownfield - Water | 515335.04
476.322 |  |  |  | DN300 DICL - Brownfield - Water
610.352 |  |  |  | DN375 DICL - Brownfield - Water
85.573 |  | 20400 | 95200 | DN100 uPVC - Greenfield - Water |  |  | 1745689.2 |  | 8146549.6
193.828 |  |  |  | DN150 DICL - Greenfield - Water
245.378 |  |  |  | DN200 DICL - Greenfield - Water
245.378 |  | 13440 |  | DN250 uPVC - Greenfield - Water |  |  | 3297880.32
338.168 |  |  |  | DN300 DICL - Greenfield - Water
430.958 |  |  |  | DN375 DICL - Greenfield - Water
513.438 |  |  | 8960 | DN450 DICL - Greenfield - Water |  |  |  |  | 4600404.48
265.998 |  |  |  | DN100 - Brownfield - Sewer
323.734 | 320 |  |  | DN150 - Brownfield - Sewer |  | 103594.88
429.927 | 1300 |  |  | DN225 - Brownfield - Sewer |  | 558905.1
566.019 |  |  |  | DN300 - Brownfield - Sewer
737.165 | 300 |  |  | DN375 - Brownfield - Sewer |  | 221149.5
900.063 |  |  |  | DN450 - Brownfield - Sewer
1037.186 |  |  |  | DN500 - Brownfield - Sewer
1310.401 |  |  |  | DN600 - Brownfield - Sewer
210.324 |  | 20000 | 100000 | DN100 - Greenfield - Sewer |  |  |  | 4206480 |  | 21032400
248.471 |  |  |  | DN150 - Greenfield - Sewer
312.393 |  | 28560 | 133280 | DN225 - Greenfield - Sewer |  |  |  | 8921944.08 |  | 41635739.04
427.865 |  |  |  | DN300 - Greenfield - Sewer
557.771 |  | 8040 | 17920 | DN375 - Greenfield - Sewer |  |  |  | 4484478.84 |  | 9995256.32
678.398 |  |  |  | DN450 - Greenfield - Sewer
786.653 |  |  |  | DN500 - Greenfield - Sewer
1018.628 |  |  | 17920 | DN600 - Greenfield - Sewer | [5 empty] | 18253813.76
106.193 |  |  |  | DN100 DICL - Sewer Pressure Pipe
106.193 |  |  |  | DN100 DICL - Sewer Pressure Pipe
152.588 |  |  |  | DN150 DICL - Sewer Pressure Pipe
183.518 |  | 1000 | 3000 | DN200 DICL - Sewer Pressure Pipe |  |  |  | 183518 |  | 550554
229.913 |  |  |  | DN250 DICL - Sewer Pressure Pipe
DN300 DICL - Sewer Pressure Pipe
DN375 DICL - Sewer Pressure Pipe
|  |  |  | Total length of reticulation network | 3160 | 1920 | 53840 | 57600 | 204160 | 272120
|  |  |  | Reticulation Capital expenditure | 796076.34 | 883649.48 | 6322009.52 | 17796420.92 | 19139154.08 | 91467763.12
|  |  |  | Average asset lives | Pipe: 100 yrs Ancillary: 30 yrs | 100 yrs | Pipe: 100 yrs Ancillary: 30 yrs | 100 yrs | Pipe: 100 yrs Ancillary: 30 yrs | 100 yrs
|  |  |  | Reticulation annual operating expenditure (New Asset) | 1643.2 | 1459.2 | 27996.8 | 43536 | 106163.2 | 206091.2
|  |  |  | Total Reticulation operating expenditure (Total Serviceable Life) | 628786.28 | 455289.6 | 10713244.72 | 13634975 | 40624369.28 | 64456676.6
Sewerage pump stations
Sewerage Pump - 10L/s
433020 |  |  |  | Sewerage Pump - 20L/s
546430 |  |  |  | Sewerage Pump - 30L/s
649530 |  |  |  | Sewerage Pump - 40L/s
742320 |  |  |  | Sewerage Pump - 50L/s
824800 |  |  |  | Sewerage Pump - 60L/s
979450 |  | 1 | 3 | Sewerage Pump - 80L/s |  |  |  | 979450 |  | 2938350
1103170 |  |  |  | Sewerage Pump - 100L/s
1340300 |  |  |  | Sewerage Pump - 140L/s
1546500 |  |  |  | Sewerage Pump - 180L/s
1649600 |  |  |  | Sewerage Pump - 200L/s
|  |  |  | Sewerage pump station capital expenditure |  |  |  | 979450 |  | 2938350
|  |  |  | Average asset lives |  |  |  | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 20 years |  | Pumps: 25 years Pipeworks: 50 years Valves: 30 years Struct: 100 years EI&C: 20 years
|  |  |  | Total reticulation capital expenditure (inc. sewerage pumps) | 796076.34 | 883649.48 | 6322009.52 | 18775870.92 | 19139154.08 | 94406113.12
Water distribution (likely requirements)
2165100 |  | 1 | 2 | Water Service Reservoirs - 10ML |  |  | 2165100 |  | 4330200
381470 |  | 1 | 2 | Water Pumping Station - 100kW |  |  | 381470 |  | 762940
|  |  |  | Water distribution capital expenditure |  |  | 2546570 |  | 5093140
|  |  |  | Average asset lives |  |  | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years |  | Pumps: 20 years Pipeworks: 100 years Valves: 30 years EI&C: 15-25 years
|  |  |  | Pumping annual operating expenditure |  |  | 0 | 0 | 0 | 0
|  |  |  | Total Capital Expenditure (exc. Water Distribution) |  | 2319725.82 |  | 25997880.44 |  | 118045267.2
|  |  |  | Total Operating Expenditure (exc. Water Distribution) |  | 359525.6 |  | 422956 |  | 1137889.2
|  |  |  | Capex per property (exc. Water Distribution) |  | 1159.8629 |  | 12998.9402 |  | 11804.5267
|  |  |  | Opex per property (exc. Water Distribution) |  | 179.7628 |  | 211.478 |  | 113.7889
|  |  |  | Total Capital Expenditure |  | 2319725.82 |  | 28544450.44 |  | 123138407.2
|  |  |  | Total Operating Expenditure |  | 359525.6 |  | 422956 |  | 1137889.2
|  |  |  | Capex per property |  | 1159.8629 |  | 14272.2252 |  | 12313.8407
|  |  |  | Opex per property |  | 179.7628 |  | 211.478 |  | 113.7889
Note on F22: Tim Ryan: These costs are annual and for the provision of both water and wastewater
Note on F80: Tim Ryan: We have assumed that sewerage pump will be required for greenfield developments to ensure suitable discharge of sewage from the reticulation network. This will not always be the case and will be dependent on individual circumstances for the development, however we think it is reasonable that pumping would be required for reticulation services in greenfield developments.

## Operating Cost Summary
OPERATING COST SUMMARY
| Total Lifecycle Cost (100 yrs) |  | Opex Cost - New Asset |  | Lifecycle Cost Breakdown
Item | Cost | UoM | Cost | UoM | Cost | UoM | Remarks | Reference
Water main | 198.983 | per m | 0.52 | per m | 1.9898 | per m |  | 2013-14 Water Supply and Sewerage NSW Benchmarking Report, Table 13
[5 empty] | 50 | '000 / 100km | Operation Cost
[5 empty] | 143 | '000 / 100km | Maintenance cost
Water Pump Station | 2680600 | each | 26806 | each | 26806 | each
[5 empty] | 3 | '000 / Pump | Operation Cost
[5 empty] | 5 | '000 / Pump | Maintenance cost
[5 empty] | 18 | '000 / Pump | Energy Cost
Water Reservoir | 927.9 | per connection | 9.279 | per property | 9.279 | per property
[5 empty] | 9 | per property
Gravity Sewer Main | 237.13 | per m | 0.76 | per m | 2.3713 | per m |  | 2013-14 Water Supply and Sewerage NSW Benchmarking Report, Table 18
[5 empty] | 73 | '000 / 100km | Operation Cost
[5 empty] | 157 | '000 / 100km | Maintenance cost
Pressure Sewer Main | 213.417 | per m | 0.52 | per m | 2.1342 | per m |  | Operational Cost based on 2013-14 Water Supply and Sewerage NSW Benchmarking Report, Table 18 Maintenance cost based on water main (pressure main)
[5 empty] | 50 | '000 / 100km | Operation Cost
[5 empty] | 157 | '000 / 100km | Maintenance cost
Sewer Pump Station | 1443400 | each | 14434 | each | 14434 | each |  | 2013-14 Water Supply and Sewerage NSW Benchmarking Report, Table 18
[5 empty] | 5 | '000 / Pump | Operation Cost
[5 empty] | 5 | '000 / Pump | Maintenance cost
[5 empty] | 4 | '000 / Pump | Energy Cost

## Renewal Costs
RENEWAL COSTS
Renewal Cost
Service | Asset | UNIT | CAPEX $/m | 60% OF CAPEX (Removal) (1) $/m | GREENFIELD (Installation of new) (2) $/m | DIFFICULTIES (site management and traffic control) (3) $/m | EXHUME AND RELAY COST (1)+(2)+(3) $/m | RELINE COST (50% OF EXHUME AND RELAY) $/m
Water Reticulation | DN50 PVC - Brownfield - Water | Metre | 107.224 | 64.3344 | 63.922 | 43.302 | 171.5584 | n/a
Water Reticulation | DN80 PVC - Brownfield - Water | Metre | 125.782 | 75.4692 | 82.48 | 43.302 | 201.2512 | n/a
Water Reticulation | DN100 PVC - Brownfield - Water | Metre | 141.247 | 84.7482 | 97.945 | 43.302 | 225.9952 | n/a
Water Reticulation | DN150 PVC - Brownfield - Water | Metre | 207.231 | 124.3386 | 144.34 | 62.891 | 331.5696 | n/a
Water Reticulation | DN200 PVC - Brownfield - Water | Metre | 279.401 | 167.6406 | 195.89 | 83.511 | 447.0416 | n/a
Water Reticulation | DN250 PVC - Brownfield - Water | Metre | 362.912 | 217.7472 | 257.75 | 105.162 | 580.6592 | n/a
Water Reticulation | DN300 PVC - Brownfield - Water | Metre | 455.702 | 273.4212 | 329.92 | 125.782 | 729.1232 | n/a
Water Reticulation | DN375 PVC - Brownfield - Water | Metre | 600.042 | 360.0252 | 433.02 | 167.022 | 960.0672 | n/a
Water Reticulation | DN100 DICL - Brownfield - Water | Metre | 208.262 | 124.9572 | 164.96 | 43.302 | 333.2192 | n/a
Water Reticulation | DN150 DICL - Brownfield - Water | Metre | 269.091 | 161.4546 | 206.2 | 62.891 | 430.5456 | n/a
Water Reticulation | DN200 DICL - Brownfield - Water | Metre | 341.261 | 204.7566 | 257.75 | 83.511 | 546.0176 | n/a
Water Reticulation | DN250 DICL - Brownfield - Water | Metre | 404.152 | 242.4912 | 298.99 | 105.162 | 646.6432 | n/a
Water Reticulation | DN300 DICL - Brownfield - Water | Metre | 476.322 | 285.7932 | 350.54 | 125.782 | 762.1152 | n/a
Water Reticulation | DN375 DICL - Brownfield - Water | Metre | 610.352 | 366.2112 | 443.33 | 167.022 | 976.5632 | n/a
Wastewater Reticulation - Gravity | DN100 - Brownfield - Sewer | Metre | 265.998 | 159.5988 | 222.696 | 43.302 | 425.5968 | n/a
Wastewater Reticulation - Gravity | DN150 - Brownfield - Sewer | Metre | 323.734 | 194.2404 | 260.843 | 62.891 | 517.9744 | 258.9872
Wastewater Reticulation - Gravity | DN225 - Brownfield - Sewer | Metre | 429.927 | 257.9562 | 324.765 | 105.162 | 687.8832 | 343.9416
Wastewater Reticulation - Gravity | DN300 - Brownfield - Sewer | Metre | 566.019 | 339.6114 | 440.237 | 125.782 | 905.6304 | 452.8152
Wastewater Reticulation - Gravity | DN375 - Brownfield - Sewer | Metre | 737.165 | 442.299 | 570.143 | 167.022 | 1179.464 | 589.732
Wastewater Reticulation - Gravity | DN450 - Brownfield - Sewer | Metre | 900.063 | 540.0378 | 690.77 | 209.293 | 1440.1008 | 720.0504
Wastewater Reticulation - Gravity | DN500 - Brownfield - Sewer | Metre | 1037.186 | 622.3116 | 799.025 | 238.161 | 1659.4976 | 829.7488
Wastewater Reticulation - Gravity | DN600 - Brownfield - Sewer | Metre | 1310.401 | 786.2406 | 1031 | 279.401 | 2096.6416 | 1048.3208
Wastewater Reticulation - Pressure | DN100 DICL - Sewer Pressure Pipe | Metre | 149.495 | 89.697 | 118.565 | 43.302 | 251.564 | n/a
Wastewater Reticulation - Pressure | DN150 DICL - Sewer Pressure Pipe | Metre | 215.479 | 129.2874 | 164.96 | 62.891 | 357.1384 | n/a
Wastewater Reticulation - Pressure | DN200 DICL - Sewer Pressure Pipe | Metre | 267.029 | 160.2174 | 195.89 | 83.511 | 439.6184 | n/a
Wastewater Reticulation - Pressure | DN250 DICL - Sewer Pressure Pipe | Metre | 335.075 | 201.045 | 242.285 | 105.162 | 548.492 | n/a
Wastewater Reticulation - Pressure | DN300 DICL - Sewer Pressure Pipe | Metre | 417.555 | 250.533 | 304.145 | 125.782 | 680.46 | n/a
Wastewater Reticulation - Pressure | DN375 DICL - Sewer Pressure Pipe | Metre | 567.05 | 340.23 | 412.4 | 167.022 | 919.652 | n/a
| CPI Increase | 103.1%
| % Cost of Capex for Removal | 60%
| % Cost of Exhume & Relay for Relining | 50%
Note on H13: Tim Ryan: Rates are based on NSW Reference Rates Manual
Note on J28: Tim Ryan: This has been assumed to be exhume and relay as relining for a pipe of this size is generally more difficult.

## Lifecycle Operating Costs
THE FOLLOWING WORKSHEETS PROVIDE DETAILED ANNUAL ESTIMATES OF LIFECYCLE OPERATING COSTS FOR DIFFERENT ASSET CLASSES

## Gravity Sewer Main
LIFECYCLE OPERATING COSTS - GRAVITY SEWER MAIN
Adjust the green cells as required
Sewer Gravity Main
| Points |  |  |  |  | Asset Life (Yr) | Cum. Lifecycle Cost ($/m)
| x = | y = |  |  |  | 0 | 0
(1) | 0 | 0.76 |  |  |  | 1 | 0.77513
(2) | 25 | Unknown |  |  |  | 2 | 1.5789
(3) | 80 | Unknown |  |  |  | 3 | 2.4088
(4) | 100 | Unknown |  |  |  | 4 | 3.2625
[6 empty] | 5 | 4.1379
| Equations | From | To | Percentage | Proportion | 6 | 5.0328
(5) | ∫ y dx | 0 | 100 | 100% | 237 | 7 | 5.9452
(6) | ∫ y dx | 0 | 25 | 10% | 23.7 | 8 | 6.8733
(7) | ∫ y dx | 25 | 80 | 40% | 94.8 | 9 | 7.8151
(8) | ∫ y dx | 80 | 100 | 50% | 118.5 | 10 | 8.769
[6 empty] | 11 | 9.7335
[6 empty] | 12 | 10.707
| Where: | y = ax3 + bx2 + cx + d |  | At x = 0, |  | 13 | 11.6882
|  |  |  | y = d = | 0.76 | 14 | 12.6758
[6 empty] | 15 | 13.6685
| Matrices representing system of linear equations to solve |  |  |  |  | 16 | 14.6654
| A |  |  |  | B | 17 | 15.6655
(6) | 97656.25 | 5208.3333 | 312.5 |  | 4.7 | 18 | 16.6679
(7) | 10142343.75 | 165458.3333 | 2887.5 |  | 53 | 19 | 17.6719
(8) | 14760000 | 162666.6667 | 1800 |  | 103.3 | 20 | 18.6769
[6 empty] | 21 | 19.6822
| A-1 |  |  |  | X | 22 | 20.6874
| 1.25e-06 | -3.0152e-07 | 2.6667e-07 |  | 1.7441e-05 | 23 | 21.6923
| -0.00017719 | 3.2267e-05 | -2.1e-05 |  | -0.0012919 | 24 | 22.6965
| 0.0057625 | -0.00044356 | 0.00026667 |  | 0.031122 | 25 | 23.7
[6 empty] | 26 | 24.7027
| Solving for X; | X = A-1 · B | Coefficients of y; | a = | 1.7441e-05 | 27 | 25.7048
|  |  |  | b = | -0.0012919 | 28 | 26.7064
|  |  |  | c = | 0.031122 | 29 | 27.7077
|  |  |  | d = | 0.76 | 30 | 28.7093
[6 empty] | 31 | 29.7116
| Points solved |  |  |  |  | 32 | 30.7152
| x = | y = |  |  |  | 33 | 31.7208
(1) | 0 | 0.76 |  |  |  | 34 | 32.7292
(2) | 25 | 1.0031 |  |  |  | 35 | 33.7415
(3) | 80 | 3.9114 |  |  |  | 36 | 34.7585
(4) | 100 | 8.3943 |  |  |  | 37 | 35.7814
[6 empty] | 38 | 36.8116
[6 empty] | 39 | 37.8502
[6 empty] | 40 | 38.8987
[6 empty] | 41 | 39.9588
[6 empty] | 42 | 41.0319
[6 empty] | 43 | 42.1201
[6 empty] | 44 | 43.2249
[6 empty] | 45 | 44.3485
[6 empty] | 46 | 45.493
[6 empty] | 47 | 46.6604
[6 empty] | 48 | 47.8531
[6 empty] | 49 | 49.0734
[6 empty] | 50 | 50.3239
[6 empty] | 51 | 51.6072
[6 empty] | 52 | 52.9259
[6 empty] | 53 | 54.2828
[6 empty] | 54 | 55.681
[6 empty] | 55 | 57.1233
[6 empty] | 56 | 58.6129
[6 empty] | 57 | 60.153
[6 empty] | 58 | 61.7469
[6 empty] | 59 | 63.3982
[6 empty] | 60 | 65.1103
[6 empty] | 61 | 66.8868
[6 empty] | 62 | 68.7316
[6 empty] | 63 | 70.6484
[6 empty] | 64 | 72.6413
[6 empty] | 65 | 74.7142
[6 empty] | 66 | 76.8714
[6 empty] | 67 | 79.1171
[6 empty] | 68 | 81.4557
[6 empty] | 69 | 83.8916
[6 empty] | 70 | 86.4295
[6 empty] | 71 | 89.0741
[6 empty] | 72 | 91.8301
[6 empty] | 73 | 94.7025
[6 empty] | 74 | 97.6962
[6 empty] | 75 | 100.8164
[6 empty] | 76 | 104.0682
[6 empty] | 77 | 107.457
[6 empty] | 78 | 110.9882
[6 empty] | 79 | 114.6673
[6 empty] | 80 | 118.5
[6 empty] | 81 | 122.492
[6 empty] | 82 | 126.6491
[6 empty] | 83 | 130.9773
[6 empty] | 84 | 135.4827
[6 empty] | 85 | 140.1713
[6 empty] | 86 | 145.0495
[6 empty] | 87 | 150.1235
[6 empty] | 88 | 155.4
[6 empty] | 89 | 160.8854
[6 empty] | 90 | 166.5864
[6 empty] | 91 | 172.5098
[6 empty] | 92 | 178.6626
[6 empty] | 93 | 185.0516
[6 empty] | 94 | 191.684
[6 empty] | 95 | 198.567
[6 empty] | 96 | 205.7078
[6 empty] | 97 | 213.114
[6 empty] | 98 | 220.793
[6 empty] | 99 | 228.7524
[6 empty] | 100 | 237
NOTES:
1. Gravity sewer mains using current technology (ie. PVC rubber ring jointed) have been installed only for a relatively short time compared to old technology (eg. vitreous clay pipe). The whole life cycle cost for new sewers is not known, as the design life has not yet been reached. Hence predicting the future of the new sewers is can only be based on the assumption that there will be some degradation of the sewers over time, which will increase with age. When and where (in time) this would start cannot be determined at this stage and will only be known in the future. The below may represent a reasonable approach to the profile of cost over time.
The total lifecycle cost calculated based on the following assumptions:
  Zero maintenance cost when asset is new (i.e. operational cost only);
  10% of total lifecycle cost will be spent in the first 25 years of serviceable life to account for general operation and maintenance;
  40% of total lifecycle cost will be spent between year 26 to 80 to account for the increase of main repairs and maintenance (e.g. clearing blockage) due to ageing asset; and
  50% of total lifecycle cost will be spent in the last 20 years of the asset's serviceable life to account for large quantity of main repairs and maintenance.
2. The total lifecycle cost was estimated based on the 2013-14 Water Supply and Sewerage NSW Benchmarking Report.

## Pressure Sewer Main
LIFECYCLE OPERATING COSTS - PRESSURE SEWER MAIN
Adjust the green cells as required
Sewer Pressure Main
| Points |  |  |  |  | Asset Life (Yr) | Cum. Lifecycle Cost ($/m)
| x = | y = |  |  |  | 0 | 0
(1) | 0 | 0.52 |  |  |  | 1 | 0.56928
(2) | 30 | Unknown |  |  |  | 2 | 1.2339
(3) | 90 | Unknown |  |  |  | 3 | 1.9893
(4) | 100 | Unknown |  |  |  | 4 | 2.8307
[6 empty] | 5 | 3.7538
| Equations | From | To | Percentage | Proportion | 6 | 4.7542
(5) | ∫ y dx | 0 | 100 | 100% | 213 | 7 | 5.8275
(6) | ∫ y dx | 0 | 30 | 20% | 42.6 | 8 | 6.9698
(7) | ∫ y dx | 30 | 90 | 60% | 127.8 | 9 | 8.177
(8) | ∫ y dx | 90 | 100 | 20% | 42.6 | 10 | 9.4451
[6 empty] | 11 | 10.7704
[6 empty] | 12 | 12.1492
| Where: | y = ax3 + bx2 + cx + d |  | At x = 0, |  | 13 | 13.578
|  |  |  | y = d = | 0.52 | 14 | 15.0532
[6 empty] | 15 | 16.5716
| Matrices representing system of linear equations to solve |  |  |  |  | 16 | 18.1299
| A |  |  |  | B | 17 | 19.725
(6) | 202500 | 9000 | 450 |  | 27 | 18 | 21.3539
(7) | 16200000 | 234000 | 3600 |  | 96.6 | 19 | 23.0137
(8) | 8597500 | 90333.3333 | 950 |  | 37.4 | 20 | 24.7017
[6 empty] | 21 | 26.4152
| A-1 |  |  |  | X | 22 | 28.1516
| 8.0658e-07 | -2.5162e-07 | 5.7143e-07 |  | 1.8843e-05 | 23 | 29.9085
| -0.00012198 | 2.8818e-05 | -5.1429e-05 |  | -0.0024329 | 24 | 31.6836
| 0.0042988 | -0.00046314 | 0.00077143 |  | 0.10018 | 25 | 33.4746
[6 empty] | 26 | 35.2795
| Solving for X; | X = A-1 · B | Coefficients of y; | a = | 1.8843e-05 | 27 | 37.0964
|  |  |  | b = | -0.0024329 | 28 | 38.9232
|  |  |  | c = | 0.10018 | 29 | 40.7583
|  |  |  | d = | 0.52 | 30 | 42.6
[6 empty] | 31 | 44.4468
| Points solved |  |  |  |  | 32 | 46.2973
| x = | y = |  |  |  | 33 | 48.1501
(1) | 0 | 0.52 |  |  |  | 34 | 50.0042
(2) | 30 | 1.8445 |  |  |  | 35 | 51.8583
(3) | 90 | 3.5661 |  |  |  | 36 | 53.7115
(4) | 100 | 5.0518 |  |  |  | 37 | 55.5631
[6 empty] | 38 | 57.4121
[6 empty] | 39 | 59.2581
[6 empty] | 40 | 61.1005
[6 empty] | 41 | 62.9389
[6 empty] | 42 | 64.773
[6 empty] | 43 | 66.6027
[6 empty] | 44 | 68.4278
[6 empty] | 45 | 70.2485
[6 empty] | 46 | 72.0648
[6 empty] | 47 | 73.8772
[6 empty] | 48 | 75.6859
[6 empty] | 49 | 77.4915
[6 empty] | 50 | 79.2945
[6 empty] | 51 | 81.0958
[6 empty] | 52 | 82.8962
[6 empty] | 53 | 84.6965
[6 empty] | 54 | 86.498
[6 empty] | 55 | 88.3017
[6 empty] | 56 | 90.109
[6 empty] | 57 | 91.9213
[6 empty] | 58 | 93.7401
[6 empty] | 59 | 95.567
[6 empty] | 60 | 97.4038
[6 empty] | 61 | 99.2524
[6 empty] | 62 | 101.1146
[6 empty] | 63 | 102.9927
[6 empty] | 64 | 104.8887
[6 empty] | 65 | 106.8051
[6 empty] | 66 | 108.7443
[6 empty] | 67 | 110.7087
[6 empty] | 68 | 112.701
[6 empty] | 69 | 114.7241
[6 empty] | 70 | 116.7807
[6 empty] | 71 | 118.874
[6 empty] | 72 | 121.0068
[6 empty] | 73 | 123.1826
[6 empty] | 74 | 125.4047
[6 empty] | 75 | 127.6763
[6 empty] | 76 | 130.0013
[6 empty] | 77 | 132.3831
[6 empty] | 78 | 134.8256
[6 empty] | 79 | 137.3326
[6 empty] | 80 | 139.9083
[6 empty] | 81 | 142.5567
[6 empty] | 82 | 145.282
[6 empty] | 83 | 148.0886
[6 empty] | 84 | 150.9809
[6 empty] | 85 | 153.9636
[6 empty] | 86 | 157.0413
[6 empty] | 87 | 160.2188
[6 empty] | 88 | 163.5011
[6 empty] | 89 | 166.8931
[6 empty] | 90 | 170.4
[6 empty] | 91 | 174.0271
[6 empty] | 92 | 177.7796
[6 empty] | 93 | 181.6632
[6 empty] | 94 | 185.6833
[6 empty] | 95 | 189.8458
[6 empty] | 96 | 194.1563
[6 empty] | 97 | 198.6209
[6 empty] | 98 | 203.2456
[6 empty] | 99 | 208.0366
[6 empty] | 100 | 213
NOTES:
1. Sewer rising mains are more complicated to operate compared to clear water reticulation mains due to the solids in the sewage, which can cause siltation and blockage of the main. More operator attendance is required to ensure the main operates reliably. The total lifecycle cost was calculated based on the following assumptions:
  Zero maintenance cost when asset is new (i.e. operational cost only);
  20% of total lifecycle cost will be spent in the first 30 years of serviceable life to account for general operation and maintenance;
  60% of total lifecycle cost will be spent between year 31 to 90 to account for the increased maintenance and monitoring of hte asset (e.g., main repair and replacement and inspections) due to asset ageing; and
  The remaining 20% of total lifecycle cost will be spent in the last 10 years of the asset's serviceable life to account for main repairs.
2. The total lifecycle cost was estimated based on the 2013-14 Water Supply and Sewerage NSW Benchmarking Report.

## Water Main
LIFECYCLE OPERATING COSTS - WATER MAIN
Adjust the green cells as required
Water Main
| Points |  |  |  |  | Asset Life (Yr) | Cum. Lifecycle Cost ($/m)
| x = | y = |  |  |  | 0 | 0
(1) | 0 | 0.52 |  |  |  | 1 | 0.51782
(2) | 30 | Unknown |  |  |  | 2 | 1.0324
(3) | 90 | Unknown |  |  |  | 3 | 1.5452
(4) | 100 | Unknown |  |  |  | 4 | 2.0579
[6 empty] | 5 | 2.5721
| Equations | From | To | Percentage | Proportion | 6 | 3.0891
(5) | ∫ y dx | 0 | 100 | 100% | 199 | 7 | 3.6106
(6) | ∫ y dx | 0 | 30 | 10% | 19.9 | 8 | 4.138
(7) | ∫ y dx | 30 | 90 | 70% | 139.3 | 9 | 4.6726
(8) | ∫ y dx | 90 | 100 | 20% | 39.8 | 10 | 5.2161
[6 empty] | 11 | 5.7697
[6 empty] | 12 | 6.3348
| Where: | y = ax3 + bx2 + cx + d |  | At x = 0, |  | 13 | 6.9128
|  |  |  | y = d = | 0.52 | 14 | 7.5049
[6 empty] | 15 | 8.1126
| Matrices representing system of linear equations to solve |  |  |  |  | 16 | 8.737
| A |  |  |  | B | 17 | 9.3795
(6) | 202500 | 9000 | 450 |  | 4.3 | 18 | 10.0413
(7) | 16200000 | 234000 | 3600 |  | 108.1 | 19 | 10.7235
(8) | 8597500 | 90333.3333 | 950 |  | 34.6 | 20 | 11.4273
[6 empty] | 21 | 12.154
| A-1 |  |  |  | X | 22 | 12.9046
| 8.0658e-07 | -2.5162e-07 | 5.7143e-07 |  | -3.96e-06 | 23 | 13.6803
| -0.00012198 | 2.8818e-05 | -5.1429e-05 |  | 0.00081134 | 24 | 14.4821
| 0.0042988 | -0.00046314 | 0.00077143 |  | -0.0048892 | 25 | 15.3111
[6 empty] | 26 | 16.1684
| Solving for X; | X = A-1 · B | Coefficients of y; | a = | -3.96e-06 | 27 | 17.0549
|  |  |  | b = | 0.00081134 | 28 | 17.9718
|  |  |  | c = | -0.0048892 | 29 | 18.9198
|  |  |  | d = | 0.52 | 30 | 19.9
[6 empty] | 31 | 20.9133
| Points solved |  |  |  |  | 32 | 21.9606
| x = | y = |  |  |  | 33 | 23.0428
(1) | 0 | 0.52 |  |  |  | 34 | 24.1607
(2) | 30 | 0.99661 |  |  |  | 35 | 25.3151
(3) | 90 | 3.765 |  |  |  | 36 | 26.5069
(4) | 100 | 4.1845 |  |  |  | 37 | 27.7368
[6 empty] | 38 | 29.0056
[6 empty] | 39 | 30.314
[6 empty] | 40 | 31.6628
[6 empty] | 41 | 33.0525
[6 empty] | 42 | 34.484
[6 empty] | 43 | 35.9577
[6 empty] | 44 | 37.4743
[6 empty] | 45 | 39.0345
[6 empty] | 46 | 40.6387
[6 empty] | 47 | 42.2875
[6 empty] | 48 | 43.9815
[6 empty] | 49 | 45.7211
[6 empty] | 50 | 47.5068
[6 empty] | 51 | 49.339
[6 empty] | 52 | 51.2182
[6 empty] | 53 | 53.1447
[6 empty] | 54 | 55.119
[6 empty] | 55 | 57.1414
[6 empty] | 56 | 59.2122
[6 empty] | 57 | 61.3318
[6 empty] | 58 | 63.5003
[6 empty] | 59 | 65.7181
[6 empty] | 60 | 67.9854
[6 empty] | 61 | 70.3024
[6 empty] | 62 | 72.6693
[6 empty] | 63 | 75.0862
[6 empty] | 64 | 77.5533
[6 empty] | 65 | 80.0707
[6 empty] | 66 | 82.6385
[6 empty] | 67 | 85.2568
[6 empty] | 68 | 87.9255
[6 empty] | 69 | 90.6448
[6 empty] | 70 | 93.4146
[6 empty] | 71 | 96.2348
[6 empty] | 72 | 99.1055
[6 empty] | 73 | 102.0266
[6 empty] | 74 | 104.9979
[6 empty] | 75 | 108.0193
[6 empty] | 76 | 111.0908
[6 empty] | 77 | 114.212
[6 empty] | 78 | 117.3829
[6 empty] | 79 | 120.6031
[6 empty] | 80 | 123.8725
[6 empty] | 81 | 127.1909
[6 empty] | 82 | 130.5578
[6 empty] | 83 | 133.973
[6 empty] | 84 | 137.4361
[6 empty] | 85 | 140.9468
[6 empty] | 86 | 144.5048
[6 empty] | 87 | 148.1095
[6 empty] | 88 | 151.7606
[6 empty] | 89 | 155.4576
[6 empty] | 90 | 159.2
[6 empty] | 91 | 162.9873
[6 empty] | 92 | 166.8191
[6 empty] | 93 | 170.6947
[6 empty] | 94 | 174.6135
[6 empty] | 95 | 178.575
[6 empty] | 96 | 182.5786
[6 empty] | 97 | 186.6235
[6 empty] | 98 | 190.7092
[6 empty] | 99 | 194.835
[6 empty] | 100 | 199
NOTES:
1. The total lifecycle cost calculated based on the following assumptions:
  Zero maintenance cost when asset is new (i.e. operational cost only);
  10% of total lifecycle cost will be spent in the first 30 years of serviceable life to account for general operation and maintenance (e.g., leak repair and main breaks);
  70% of total lifecycle cost will be spent between year 31 to 90 to account for two sets of valve replacement (on an assumed 30-year valve life) and increased pipeline repair and replacement due to ageing asset; and
  The remaining 20% of total lifecycle cost will be spent in the last 10 years of the asset's serviceable life to account for pipeline repair due to ageing asset.
2. The total lifecycle cost was estimated based on the 2013-14 Water Supply and Sewerage NSW Benchmarking Report.

## Name Ranges (hidden)
Service_Names
Water Retail
Water Reticulation
Wastewater Retail
Wastewater Reticulation - Gravity
Wastewater Reticulation - Pressure