## Contents (hidden)
Chapters
Information
Category
Water Quality
System Continuity & Reliability
Environmental Performance
Customers
References
Appendices
System Continuity & Reliability

## Information
INFORMATION SHEET FOR USING THE INDICATOR DATABASE
Indicator Codes found in this database:
AM | Asset management
BH | Biodiversity and habitats
EF | Environmental flows
FRWQ | Fish River water quality
HWC | Hunter Water Corporation
IPART | IPART indicator or system performance standard as detailed in IPART issued operating licence or reporting manual
NWI | National Water Initiative indicator
OL | Operating licence
PF | Policing functions
RH | River health
RT | Response time
SCA | Sydney Catchment Authority
SPS | System performance standard
SW | Surface Water
SWC | Sydney Water Corporation
SWF | Surface water flow
WA | Water availability
WD | Water delivery
WQ | Water quality
Each datapoint has a hyperlink next to it:
Clicking on the number will take the user to a reference list. This reference list provides bibliographic information about the data source. This data can also be accessed by clicking the "References" tab.
Cells that have a red flag (example below) have a comment including important information about the data in the cell:
Hover over the cell with the mouse to show the comment.
Data which has been reported as zero is denoted "0"
When there is no data it is denoted as ' - '
An indicator that is not applicable for a given year or utility is denoted as N/A or greyed out box
Data can be filtered by any of the fields such as utility, indicator number, indicator type (IPART or NWI). Click on the arrow of the column header of the field you wish to filter by. Select the values you wish to display from the check list
Indicators have been numbered as per the 2013 Reporting Manuals. This has meant that the numbering for a small number of indicators has changed from previous years.
Both the current numbering and previous years numbering are presented in the second and third columns of each table.
Where an indicator is new or an indicator has ceased a dash ( - ) is placed in the relevant column
NOTE: | From 1 January 2015 State Water Corporation and Sydney Catchment Authority Merged under the Water NSW Act 2014, In the 2013/14 reporting period (to which the presented data relates) the utilities were still separate. From the 2014/15 period data will be reported for both these utilties as "Water NSW"
End of information

## Water Quality
Chapter 1 : Water Quality
Indicator |  |  |  | Utility | 2005/06 |  | 2006/07 |  | 2007/08 |  | 2008/09 |  | 2009/10 |  | 2010/11 |  | 2011/12 |  | 2012/13 |  | 2013/14 |  | 2014/15 |  | 2015/16 |  | Notes/ Comments
Type | NEW No. | Prev. No. | Description
IPART | WQ1(H)(a) | WQ1(H)(a) | Microbiological compliance - percentage of routine water quality samples that comply with the ADWG for E.Coli | Hunter Water | 99.6% | 1 | 99.8% | 2 | 99.5% | 3 | 99.6% | 63 | 99.9% | 5 | 99.4% | 6 | 100% | 7 | 99.9% | 63 | 99.9% | 94 | 100% | 102 | 99.9% | 110
IPART | WQ1(H)(b) | WQ1(H)(b) | Chem/Phys - percentage of routine water quality samples that comply with the ADWG for key Chem/Phys. parameters | Hunter Water | Full compliance | 1 | Full compliance | 2 | Full compliance | 3 | 99.6% | 63 | 99.6% | 63 | 99.9% | 63 | 99.9% | 63 | 99.9% | 63 | 99.7% | 94 | 99.6% | 102 | 99.3% | 110
IPART | SCA H1 | SCA H1 | Water quality in catchment waterways in the catchment area measured against the applicable water quality objectives specified in the Australian and New Zealand Guidelines for Fresh and Marine Water Quality 2000 | WaterNSW (SCA) | Chapter 7 | 78 | Chapter 7 | 79 | Chapter 5 & 6 | 80 | Chapters 5 & 6 | 81 | Chapters 5 & 6 | 82 | Chapter 5 | 10 | Chapter 5 | 84 | Chapter 5 | 19 | Chapter 5 | 99 | Chapter 4 & 5 | 108 | Chapters 4 & 5 | 117
IPART | SCA H2 | SCA H2 | Occurrence of Cryptosporidium and Giardia cysts or oocysts in catchment waterways. [Note: Occurrence of cysts is to be measured by the number of incidences of Cryptosporidium and Giardia in the high (>1000cysts / L), medium (100 - 1000 cysts / L), and Low (<100cysts / L) categories] | WaterNSW (SCA) | Table A6 | 9 | Table A6 | 9 | Table A6 | 9 | Table A6 | 9 | Table A6 | 9 | Table A.3 | 83 | Tables A6, A12, A18, A24, A48, A73, A87, A106 | 11 | Tables A6, A12, A19, A27, A51, A105 | 89 | Tables A6,A13, A21, A40, A85 | 99 | Tables A6, A22, A42, A97 | 109 | Tables A6, A13, A21, A40, A83 | 118 | Statistical analysis methods were updated in 2009/10. Reference #90 provides details of this. Historic data reported here is as presented in 2009/10 report.
IPART | WQ-RH-E | WQ-RH-E | Turbidity, pH, EC, Total Al, Total Fe, Total N, Total P, Nox, NH4, FRP, Chlorophyll a, DO and water temperature - assessed against AZ+NZECC/ARMCANZ (2000) guidelines | WaterNSW (SCA) | Chapters 2.1 & 2.2 | 73 |  |  | Chapter 3.1 & 3.2 | 72 |  |  |  |  | Chapter 6.1 | 71 |  |  | Chapter 5.1 | 70 | [6 empty] | Catchment audits are not undertaken on an annual basis.
IPART | WQ-RH-C | WQ-RH-C | Compliance with recreational guidelines cyanobacteria for SCA storages only | WaterNSW (SCA) | Chapter 2.3 | 73 |  |  | Chapter 3.3 | 72 |  |  |  |  | Chapter 6.3 | 71 |  |  | Chapter 5.3 | 70 | [6 empty] | Catchment audits are not undertaken on an annual basis.
IPART | - | FRWQ | Percentage of treated water samples that comply with ADWG (2004) at the Fish River Scheme's water sampling locations for e-coli, colour, turbidity, iron, manganese, aluminium and pH | WaterNSW (State Water) | [22 empty] | Filtered water data has been reported for this indicator.
|  |  | E.Coli | WaterNSW (State Water) | 98% | 12 | 97.2% | 68 | 97.8% | 13 | 99.3% | 14 | 97.6% | 15 | 98.6% | 16 | 100% | 17 | 99% | 18
|  |  | Total Coliforms | WaterNSW (State Water) | - |  | - |  | - |  | - |  | - |  | - |  | - |  | 85% | 18
|  |  | Colour | WaterNSW (State Water) | 92% | 12 | 62.5% | 68 | 90% | 13 | 75% | 14 | 91.7% | 15 | 75% | 16 | 100% | 17 | 73% | 18
|  |  | Turbidity | WaterNSW (State Water) | 100% | 12 | 100% | 68 | 100% | 13 | 100% | 14 | 100% | 15 | 50% | 16 | 100% | 17 | 100% | 18
|  |  | Iron | WaterNSW (State Water) | 100% | 12 | 100% | 68 | 100% | 13 | 100% | 14 | 100% | 15 | 75% | 16 | 100% | 17 | 100% | 18
|  |  | Manganese | WaterNSW (State Water) | 100% | 12 | 75% | 68 | 60% | 13 | 88% | 14 | 66.7% | 15 | 100% | 16 | 100% | 17 | 100% | 18
|  |  | Licence Standard (% responded to within 6 hours) | WaterNSW (State Water) | 100% | 12 | 100% | 68 | 100% | 13 | 100% | 14 | 100% | 15 | 75% | 16 | 100% | 17 | 100% | 18
|  |  | pH | WaterNSW (State Water) | 100% | 12 | 100% | 68 | 100% | 13 | 88% | 14 | 100% | 15 | 50% | 16 | 100% | 17 | 96% | 18
NWI | H3 | H3 | Percentage of population where microbiological compliance was achieved | Sydney Water | 100% | 22 | 100% | 49 | 100% | 49 | 100% | 49 | 100% | 49 | 100% | 49 | 100% | 48 | 100% | 66 | 100% | 93 | 100% | 103 | 100% | 112
NWI | H3 | H3 | Percentage of population where microbiological compliance was achieved | Hunter Water | 99.6% | 22 | 99.8% | 21 | 100% | 21 | 100% | 21 | 100% | 21 | 100% | 21 | 100% | 21 | 100% | 63 | 100% | 94 | 100% | 102 | 100% | 110
NWI | H4 | H4 | Number of zones where chemical compliance was achieved | Sydney Water | 13 of 13 | 22 | 13 of 13 | 49 | 13 of 13 | 49 | 13 of 13 | 49 | 13 of 13 | 49 | 13 of 13 | 49 | 12 of 13 | 48 | 12 of 13 | 66 | 13 of 13 | 93 | 13 of 13 | 103 | 13 of 13 | 112
NWI | H4 | H4 | Number of zones where chemical compliance was achieved | Hunter Water | 3 of 3 | 22 | 3 of 3 | 21 | 4 of 4 | 21 | 5 of 5 | 21 | 5 of 5 | 21 | 5 of 5 | 21 | 5 of 5 | 21 | 5 of 5 | 63 | 5 of 5 | 94 | 5 of 5 | 102 | 5 of 5 | 110
NWI | C9 | C9 | Water quality complaints (no. per 1000 properties) | Sydney Water | 0.8 | 22 | 0.8 | 49 | 0.9 | 49 | 0.6 | 49 | 0.7 | 49 | 0.6 | 49 | 0.5 | 48 | 0.5 | 66 | 0.3 | 93 | 0.2 | 103 | 0.1 | 112
NWI | C9 | C9 | Water quality complaints (no. per 1000 properties) | Hunter Water | 6.8 | 22 | 3.9 | 21 | 2.8 | 21 | 3.24 | 21 | 3.44 | 21 | 2.79 | 21 | 2.8652 | 21 | 2.9 | 63 | 3.3 | 94 | 3 | 102 | 1.7 | 110
End of Water Quality data

## System Continuity & Reliability
Chapter 2: System Continuity and Reliability
Indicator/System Performance Standard |  |  |  | Utility | 2005/06 |  | 2006/07 |  | 2007/08 |  | 2008/09 |  | 2009/10 |  | 2010/11 |  | 2011/12 |  | 2012/13 |  | 2013/14 |  | 2014/15 |  | 2015/16 |  | Notes/Comments
Type | NEW No. | Prev. No. | Description
IPART | SPS 1 | SPS 1 | Number of properties that experience a water pressure failure, as defined in: • clause 4.2.1 of the 2015-2020 Operating Licence, • clause 3.3.1 of the 2010-2015 Operating Licence, • clause 4.1.2 of the 2005-2010 Operating Licence in the preceding financial year | Sydney Water | 2540 | 24 | 1094 | 26 | 345 | 39 | 1093 | 50 | 36 | 50 | 832 | 53 | 572 | 51 | 1280 | 65 | 661 | 92 | 133 | 104 | 129 | 113
|  |  | Licence Standard (No. of properties) | Sydney Water | 15000 |  | 15000 |  | 15000 |  | 15000 |  | 15000 |  | 6000 |  | 6000 |  | 6000 |  | 6000 |  | 6000 |  | 6000
IPART | SPS 2 | SPS 2 | Number of properties that experience an unplanned water interruption exceeding 5 hours, as defined in the Operating Licence, in the preceding financial year | Sydney Water | 27805 | 24 | 29592 | 26 | 31982 | 39 | 25656 | 52 | 21050 | 52 | 30911 | 98 | 31519 | 98 | 31626 | 98 | 32568 | 92 | 37189 | 104 | 27224 | 113 | In 2015 Sydney Water corrected historical data for 2010/11-2012/13 years previously reported.
|  |  | Licence Standard (No. of properties) | Sydney Water | 35000 |  | 35000 |  | 35000 |  | 35000 |  | 35000 |  | 40000 |  | 40000 |  | 40000 |  | 40000 |  | 40000 |  | 40000
IPART | SPS 3 | SPS 3 | Number of properties that experience 3 or more unplanned water interruptions exceeding 1 hour, as defined in the Operating Licence, in the preceding financial year | Sydney Water | [10 empty] | 6271 | 98 | 5790 | 98 | 6363 | 98 | 4978 | 92 | 8005 | 104 | 6524 | 113 | This performance standard was introduced in the 2010-2015 Operating Licence. In 2015 Sydney Water corrected historical data for 2010/11-2012/13 years previously reported.
|  |  | Licence Standard (No. of properties) | Sydney Water | [10 empty] | 14000 |  | 14000 |  | 14000 |  | 14000 |  | 14000 |  | 14000
IPART | SPS 4 | SPS 4 | Number of properties (other than public properties) that experience an uncontrolled sewage overflow in dry weather, as defined in the Operating Licence, in the preceding financial year Clause 3.3.3 of the 2010-2015 Operating Licence; Clause 4.3.1 of the 2005-2010 Operating Licence | Sydney Water | 22572 | 24 | 24924 | 26 | 18148 | 39 | 16028 | 54 | 17263 | 54 | 9158 | 53 | 7708 | 51 | 6908 | 65 | 8869 | 92 | 10118 | 104 | 8874 | 113
|  |  | Licence Standard (No. of properties) | Sydney Water | 25000 |  | 25000 |  | 25000 |  | 25000 |  | 25000 |  | 14000 |  | 14000 |  | 14000 |  | 14000 |  | 14000 |  | 14000
IPART | SPS 5 | SPS 5 | Number of properties (other than public properties) that experience 3 or more uncontrolled sewage overflows in dry weather, as defined in the Operating Licence, in the preceding financial year | Sydney Water | - |  | 157 | 46 | 164 | 46 | 328 | 46 | 61 | 46 | 30 | 53 | 43 | 51 | 39 | 65 | 66 | 92 | 80 | 104 | 58 | 113
|  |  | Licence Standard (No. of properties) | Sydney Water | [10 empty] | 175 |  | 175 |  | 175 |  | 175 |  | 175 |  | 175
IPART | I9 | RT 1 | Percentage of Priority 6 breaks/leaks in drinking water mains (as defined in the Operating Licence) that Sydney Water attended within 3 hours | Sydney Water | 84% | 24 | 94.2% | 26 | 91.6% | 39 | 90.8% | 29 | 92.98% | 55 | 91% | 53 | 92% | 51 | 93% | 65 | 92% | 92 | 92% | 104 | 91% | 112 | Shifted from Response Time to Infrastructure category in 2015-16 reporting year.
|  |  | Licence Standard (% responded to within 3 hours) | Sydney Water | 90% |  | 90% |  | 90% |  | 90% |  | 90% |  | 90% |  | 90% |  | 90% |  | 90% |  | 90% |  | 90%
IPART | I10 | RT 2 | Percentage of Priority 5 breaks/leaks in drinking water mains (as defined in the Operating Licence) that Sydney Water attended within 6 hours | Sydney Water | 80% | 24 | 92.6% | 26 | 92.9% | 39 | 93.7% | 29 | 95.04% | 55 | 91.4% | 53 | 93% | 51 | 93% | 65 | 91% | 92 | 92% | 104 | 90% | 112 | Shifted from Response Time to Infrastructure category in 2015-16 reporting year.
|  |  | Licence Standard (% responded to within 6 hours) | Sydney Water | 85% |  | 85% |  | 85% |  | 85% |  | 85% |  | 90% |  | 90% |  | 90% |  | 90% |  | 90% |  | 90%
IPART | I11 | I11 | Percentage of priority 5 breaks/leaks in drinking water mains that Sydney Water responded to within 24 hours. | Sydney Water | [20 empty] | 100% | 112 | New indicator for 2015-16 reporting year.
|  |  | Licence Standard (% responded to within 24 hours) | Sydney Water | [20 empty] | 90%
IPART | I12 | RT 3 | Percentage of Priority 4 breaks/leaks in drinking water mains (as defined in the Operating Licence) that Sydney Water attended within 5 days (subject to clause 4.12.4) | Sydney Water | 91% | 24 | 96% | 26 | 96.6% | 39 | 98.3% | 29 | 98.72 | 55 | 94.1% | 53 | 92% | 51 | 91% | 65 | 94% | 92 | 91% | 104 | 91% | 112 | Shifted from Response Time to Infrastructure category in 2015-16 reporting year.
|  |  | Licence Standard (% responded to within 5 days) | Sydney Water | 100% |  | 100% |  | 100% |  | 100% |  | 100% |  | 90% |  | 90% |  | 90% |  | 90% |  | 90% |  | 90%
IPART | I1 | I1 | The number of properties affected by an unplanned water interruption duration of more than 1 hour and less than or equal to 5 hours | Sydney Water | 265639 | 24 | 247037 | 39 | 234091 | 39 | 223313 | 29 | 210497 | 46 | 185204 | 49 | 154660 | 48 | 197586 | 93 | 200955 | 93 | 227846 | 103 | 234968 | 112 | In 2015 Sydney Water corrected historical data for 2012/13 year previously reported.
IPART | I2 | I2 | Occurrence of water interruptions to affected properties (i.e. the number of properties experiencing 3 or more Planned and Unplanned water interruptions) of more than one hour duration) | Sydney Water | [14 empty] | 6003 | 93 | 5191 | 93 | 7642 | 103 | 8922 | 112 | This indicator was introduced in2012/13. Prior to this the indicator was slightly different with 1 hour durations not included. Therefore indicator reporting prior to 2012/13 has been omitted. The interpretation of this indicator changed from 1 July 2015 so it is not comparable to previous historical data.
IPART | I3 | I3 | Events leading to planned or unplanned water interruption where 250 or more properties experience an interruption of over 5hrs duration | Sydney Water | - |  | - |  | - |  | - |  | - |  | - |  | - |  | 35 | 93 | 25 | 93 | 30 | 103 | 19 | 112
IPART | I4 | I4 | The number of residential properties affected by planned water supply interruptions in peak hours (5am-9am and 5pm-11pm) | Sydney Water | [14 empty] | 18540 | 66 | 18369 | 93 | 12990 | 103 | 13061 | 112 | Sydney Water changed the methodology for calculation of this indicator in 2013/14 and revised the 2012/13 data
IPART | I5 | I5 | The number of properties in the utility’s drinking water supply network experiencing a water pressure failure which is occasional or recurrent, but not permanent | Sydney Water | 2519 | 24 | 1070 | 39 | 322 | 75 | 1070 | 29 | 14 | 46 | 805 | 48 | 543 | 48 | 1076 | 66 | 661 | 93 | 84 | 103 | 96 | 112
IPART | - | I6 | Number of Priority 6 sewage overflows responded to in a year | Sydney Water | 2462 | 39 | 4464 | 39 | 5231 | 39 | 4125 | 29 | 4714 | 46 | 4617 | 48 | 2949 | 48 | 2202 | 66 | [6 empty] | The sum of the old Indicator 12 Response times <1 hour and >1 hour for 2005-2012
IPART | I6 |  | Number of high priority sewage overflows per 100km of sewer main responded to in a year | Sydney Water | [14 empty] | 9 | 93 | 14 | 93 | 22 | 103 | 22 | 112
IPART | - | I7 | Number of Priority 5 sewage overflows responded to in a year | Sydney Water | 27590 | 39 | 26792 | 39 | 20959 | 39 | 15551 | 29 | 17087 | 46 | 17052 | 48 | 10885 | 48 | 10160 | 66 | [6 empty] | The sum of the old Indicator 12 Response times <3 hour and >3 hour for 2005-2012
IPART | I7 |  | Number of medium priority sewage overflows per 100km of sewer main responded to in a year | Sydney Water | [14 empty] | 41 | 93 | 42 | 93 | 44 | 103 | 35 | 112
IPART | I8 | I8 | Number of residential customers’ dwellings affected by sewer spills not contained within 1 hour of notification | Sydney Water | [14 empty] | 89 | 66 | 87 | 93 | 174 | 103 | 104 | 112
WATER PRESSURE STANDARD
IPART | OL4.1.1 | OL4.1.1 | The number of properties that experience a water pressure failure in a financial year (no more than 4,800) | Hunter Water | 1663 | 1 | 1655 | 2 | 1658 | 58 | 1657 | 37 | 1657 | 31 | 2334 | 56 | 1171 | 57 | 1947 | 63 | 1920 | 94 | 1345 | 102 | 1312 | 110
|  |  | Licence Standard (no more than 4,800) | Hunter Water | 4800 |  | 4800 |  | 4800 |  | 4800 |  | 4800 |  | 4800 |  | 4800 |  | 4800 |  | 4800 |  | 4800 |  | 4800
WATER CONTINUITY STANDARD
IPART | OL4.2.1(a) | OL4.2.1(a) | Number of properties that experience an unplanned water interruption that lasts more than 5 continuous hours (no more than 10,000) | Hunter Water | [6 empty] | 2762 | 63 | 1929 | 94 | 5845 | 56 | 1855 | 57 | 5464 | 63 | 2347 | 94 | 7020 | 102 | 3901 | 110
|  |  | CURRENT Licence Standard: No more than 10,000 | Hunter Water | [6 empty] | - |  | - |  | 10000 |  | 10000 |  | 10000 |  | 10000 |  | 10000 |  | 10000
|  |  | Hunter Water must ensure that no more than 14000 properties in a financial year experience one or more planned water interruptions or an unplanned water interruptions which taken together have a cumulative duration exceeding 5 hours. This is known as the water continuity standard | Hunter Water | 13133 | 1 | 15365 | 2 | 5488 | 58 | 9036 | 37 | 7163 | 31
|  |  | OLD Licence Standard: no more than 14,000 | Hunter Water | 14000 |  | 14000 |  | 14000 |  | 14000 |  | 14000
IPART | OL4.2.1(b) | OL4.2.1(b) | Number of properties that experience 3 or more unplanned water interruptions that each lasts more than 1 hour (no more that 5,000) | Hunter Water | [6 empty] | 2961 | 63 | 1250 | 94 | 2200 | 56 | 1836 | 57 | 1062 | 63 | 1653 | 94 | 1959 | 102 | 1488 | 110
|  |  | CURRENT Licence Standard (no more than 5,000) | Hunter Water | [6 empty] | - |  | - |  | 5000 |  | 5000 |  | 5000 |  | 5000 |  | 5000 |  | 5000
SEWAGE OVERFLOWS ON PRIVATE PROPERTIES STANDARD
IPART | OL4.3.1(a) | OL4.3.1(a) | Number of properties (other than public properties) experience an uncontrolled wastewater overflow in dry weather (no more than 5,000) | Hunter Water | [8 empty] | 3555 | 94 | 3723 | 56 | 2799 | 57 | 2601 | 63 | 3370 | 94 | 3469 | 102 | 2951 | 110
|  |  | Current Licence Standard (no more than 5,000) | Hunter Water | [8 empty] | - |  | 5000 |  | 5000 |  | 5000 |  | 5000 |  | 5000 |  | 5000
|  |  | Hunter Water must ensure that the number of uncontrolled Sewage overflows in a financial year (Other than on Public Properties) does not exceed 6,500 | Hunter Water | 3341 | 1 | 4158 | 2 | 3435 | 58 | 2740 | 37 | 3388 | 31 | [12 empty] | Inclusive of wet AND dry weather overflows.
|  |  | OLD Licence Standard: no more than 6500 | Hunter Water | 6500 |  | 6500 |  | 6500 |  | 6500 |  | 6500
IPART | OL4.3.1(b) | OL4.3.1(b) | Number of properties (other than public properties) that experience 3 or more uncontrolled wastewater overflows in dry weather (no more than 45) | Hunter Water | [6 empty] | 9 | 63 | 9 | 94 | 26 | 56 | 14 | 57 | 12 | 63 | 17 | 94 | 25 | 102 | 14 | 110
|  |  | CURRENT Licence Standard: no more than 45 | Hunter Water | [6 empty] | - |  | - |  | 45 |  | 45 |  | 45 | 63 | 45 |  | 45 |  | 45
IPART | I1 | I1 | The number of properties affected by an unplanned water interruption duration of more than 1 hour and less than or equal to 5 hours | Hunter Water | [6 empty] | 42671 | 63 | 43705 | 63 | 42332 | 63 | 34993 | 63 | 35870 | 63 | 48014 | 94 | 40900 | 102 | 45842 | 110
IPART | I2 | I2 | Occurrence of water interruptions to affected properties (i.e. the number of properties experiencing 3 or more planned and unplanned water interruptions) of more than one hour duration) | Hunter Water | - |  | - |  | - |  | 4301 | 63 | 2737 | 63 | 3624 | 94 | 3177 | 63 | 1834 | 63 | 2466 | 94 | 3392 | 102 | 3419 | 110
IPART | I3 | I3 | Events leading to planned or unplanned water interruption where 250 or more properties experience an interruption of over 5hrs duration | Hunter Water |  |  |  | 59 | 0 | 58 | 0 | 63 | 0 | 63 | 5 | 56 | 4 | 57 | 3 | 63 | 2 | 94 | 12 | 102 | 3 | 110
[7 empty] | TABLE 1 | [7 empty] | TABLE 2 |  | TABLE 3 |  | TABLE 4 |  | TABLE 5
IPART | I4(H) | I4(H) | The number of residential properties affected by planned water supply interruptions in peak hours (5am -11pm) | Hunter Water | - |  | - |  | - |  | 11680 | 63 | 12980 | 63 | 16844 | 56 | 17152 | 63 | 11760 | 63 | 12275 | 94 | 10935 | 102 | 20921 | 110 | This indicator was introduced in 2012/13 however the 2012/13 report provided 5 years of data. Hunter Water stated that there was a 20% increase in developer-related activity during the 2015-16 reporting year. The increase in the level of planned interruptions was influenced by this above activity (ie, shutdowns to enable new customer connections to be completed).
IPART | I5 | I5 | The number of properties in the utility’s drinking water supply network experiencing a water pressure failure which is occasional or recurrent, but not permanent | Hunter Water | [6 empty] | 1182 | 63 | 1182 | 63 | 1860 | 56 | 698 | 57 | 1473 | 63 | 1447 | 94 | 905 | 102 | 839 | 110 | This indicator was introduced in 2012/13 however the 2012/13 report provided 5 years of data.
IPART | - | I6(H) | Number of Priority 1 sewage overflows responded to in a year | Hunter Water | [6 empty] | 580 | 63 | 892 | 63 | 1138 | 63 | 904 | 63 | 764 | 63
IPART | I6 |  | Number of high priority sewage overflows per 100km of sewer main responded to in a year | Hunter Water | [8 empty] | 19.1 | 94 | 24.1 | 94 | 18.9 | 94 | 15.7 | 94 | 21.1 | 94 | 24 | 102 | 17 | 110 | Indicator introduced in 2013/14, the 2013/14 report provided 5 years of data
IPART | - | I7(H) | Number of Priority 2 sewage overflows responded to in a year | Hunter Water | [6 empty] | 2660 | 63 | 3186 | 63 | 3195 | 63 | 2473 | 63 | 2475 | 63
IPART | I7 |  | Number of medium priority sewage overflows per 100km of sewer main responded to in a year | Hunter Water | [8 empty] | 68.3 | 94 | 67.5 | 94 | 51.6 | 94 | 51 | 94 | 59.4 | 94 | 62.4 | 102 | 53.1 | 110 | Indicator introduced in 2013/14, the 2013/14 report provided 5 years of data
IPART | I8 | I8 | Number of residential customers’ dwellings affected by sewer spills not contained within 1 hour of notification | Hunter Water | [6 empty] | 2364 | 63 | 2503 | 63 | 2807 | 63 | 2334 | 63 | 2036 | 63 | 1417 | 94 | 1415 | 102 | 1146 | 110 | This indicator was introduced in 2012/13 however the 2012/13 report provided 5 years of data.
IPART | 1 | A1.WD(a) | percentage of Customers contacted within one working day of a non-complying water order being placed; Note: A "non-complying water order" is an order which does not comply with licence conditions or which contains insufficient information for State Water to supply water | WaterNSW (State Water) | N/A | 12 | - |  | 95% | 13 | 70% | 14 | 94% | 15 | 99% | 16 | 99% | 17 | 99% | 18 | 98.6% | 95 | 98.9% | 106 | 99.46% | 116 | State Water had not developed systems to record non-complying orders or time taken to contact customers with non-complying orders until 2007/08.
IPART | 2 | A1.WD(b) | percentage of complying water orders identified as being delivered outside of ±1 day of the scheduled day of delivery, as measured by customer complaints; | WaterNSW (State Water) | 0.04% | 12 |  |  | 0.005% | 13 | 0% | 14 | 1% | 15 | 0.009% | 16 | 0.001% | 17 | 0.03% | 18 | 0.007% | 95 | 0% | 106 | 0.012% | 116
IPART | 3 | A1.WD(c) | percentage of water orders rescheduled in consultation with Customers within one working day of a known shortage or delivery delay; Note: This indicator should be calculated as a percentage of the total number of water orders rescheduled due to a known shortage or delivery delay. | WaterNSW (State Water) | N/A | 12 | - |  | 100% | 13 | 100% | 14 | 51% | 15 | 100% | 16 | 52% | 17 | 47% | 18 | 68% | 95 | 53.8% | 106 | 100% | 116 | There were no systems to collect this information in 2005/06.
IPART | - | A1.WD(d) | percentage of time that daily minimum flow targets are met | WaterNSW (State Water) | 93% | 12 | 91% | 13 | 96% | 13 | 93% | 14 | [14 empty] | State Water commenced reporting against this standard by valley in 2009/10.
|  |  | Peel | WaterNSW (State Water) | [8 empty] | 93% | 15 | 100% | 16 | 100% | 17 | 100% | 18
|  |  | Namoi | WaterNSW (State Water) | [8 empty] | 100% | 15 | 100% | 16 | 100% | 17 | 100% | 18
|  |  | Gwydir | WaterNSW (State Water) | [8 empty] | 100% | 15 | 100% | 16 | 100% | 17 | 100% | 18
|  |  | Border Rivers | WaterNSW (State Water) | [8 empty] | 98% | 15 | 100% | 16 | 100% | 17 | 100% | 18
|  |  | Lower Darling | WaterNSW (State Water) | [8 empty] | 85% | 15 | 100% | 16 | - | 17 | 100% | 18
|  |  | Murray | WaterNSW (State Water) | [8 empty] | 98% | 15 | 100% | 16 | - | 17 | 100% | 18
|  |  | Murrumbidgee | WaterNSW (State Water) | [8 empty] | - |  | 93% | 16 | 100% | 17 | -
|  |  | Murrumbidgee - Darlot: | WaterNSW (State Water) | [8 empty] | - |  | - |  | - |  | 99% | 18
|  |  | Murrumbidgee - Balranald | WaterNSW (State Water) | [8 empty] | - |  | - |  | - |  | 100% | 18
|  |  | Billabong Creek | WaterNSW (State Water) | [8 empty] | - |  | 100% | 16 | 100% | 17 | -
|  |  | Hunter | WaterNSW (State Water) | [8 empty] | 100% | 15 | 100% | 16 | 100% | 17 | 100% | 18
|  |  | Paterson | WaterNSW (State Water) | [8 empty] | 100% | 15 | 100% | 16 | 100% | 17 | 100% | 18
|  |  | Bega | WaterNSW (State Water) | [8 empty] | - |  | 100% | 16 | 100% | 17 | 100% | 18
|  |  | Richmond | WaterNSW (State Water) | [8 empty] | - |  | 100% | 16 | 100% | 17 | 100% | 18
|  |  | Lachlan | WaterNSW (State Water) | [8 empty] | - |  | - |  | 100% | 17 | 100% | 18
|  |  | Macquarie and Cudgegong | WaterNSW (State Water) | [8 empty] | - |  | - |  | - |  | 100% | 18
IPART | - | A1.WD(e) | Percentage of complying intra-valley transfers processed within four working days of State Water’s receipt of correctly completed application form and fee | WaterNSW (State Water) | 56% | 12 | - |  | 65% | 13 | 86% | 14 | 91% | 15 | 96% | 16 | 99% | 17 | 98.5% | 18
IPART | 4 | - | Percentage of complying Intra-valley transfers processed within five working days of State Water's receipt of a correct application and fee | WaterNSW (State Water) | [16 empty] | 98.7% | 95 | 99.4% | 106 | 99.1% | 116 | slight change in indicator definition starting in the 2013/14 reporting year
IPART | - | B1.AM(a) | the average response time for unplanned supply interruptions (hours) | WaterNSW (State Water) | - | 12 | - |  | 1 | 13 | 0.26667 | 14 | 0.63333 | 15 | 0.75 | 16 | 0.8 | 17 | 8.8417 | 18
IPART | - | B1.AM(b) | Number of planned water supply interruptions | WaterNSW (State Water) | 2 | 12 | - |  | 1 | 13 | 0 | 14 | 0 | 15 | 0 | 16 | 5 | 17 | 0 | 18
IPART | - | B1.AM(c) | Number of unplanned water supply interruptions | WaterNSW (State Water) | 2 | 12 | - |  | 1 | 13 | 12 | 14 | 0 | 15 | 3 | 16 | 9 | 17 | 12 | 18
IPART | - | B1.AM(d) | Average duration of planned water supply interruptions (hours) | WaterNSW (State Water) | 8 | 12 | - |  | 48 | 13 | N/A | 14 | N/A | 15 | N/A | 16 | 149.6 | 17 | N/A | 18
IPART | - | B1.AM(e) | Average duration of unplanned water supply interruptions (hours) | WaterNSW (State Water) | 10 | 12 | - |  | 45 | 13 | 45 | 14 | N/A | 15 | 50.75 | 16 | 68 | 17 | 27.3333 | 18
IPART | - | 2.WD | Percentage of time that daily minimum flow targets are met (Fish River only) | WaterNSW (State Water) | - | 12 | - |  | N/A | 13 | N/A | 14 | N/A | 15 | N/A | 16 | - | 17 | -
| - |  | Duckmaloi Weir (min 3 MLD) | WaterNSW (State Water) | [12 empty] | 99.7% | 17 | 100% | 18
| - |  | Oberon Dam (min 2.4 MLD) | WaterNSW (State Water) | [12 empty] | 100% | 17 | 100% | 18
NWI | A8 | A8 | Water main breaks (No. per 100km of water main) | Sydney Water | 42 | 22 | 35 | 49 | 30 | 48 | 34 | 48 | 28 | 48 | 28 | 48 | 22 | 48 | 29 | 20 | 30 | 93 | 26 | 103 | 26 | 112
NWI | A10 | A10 | Real losses (L/service connection/d) | Sydney Water | 91 | 22 | 94 | 49 | 91 | 48 | 81 | 48 | 73 | 48 | 79 | 48 | 85 | 48 | 87 | 20 | 81 | 93 | 74 | 103 | 76 | 112
NWI | A14 | A14 | Sewerage main breaks and chokes (No. per 100 km of sewer main) | Sydney Water | 87.12 | 22 | 90 | 49 | 64 | 48 | 51 | 48 | 56 | 48 | 57 | 48 | 49 | 48 | 46 | 20 | 61 | 93 | 69 | 103 | 58 | 112
NWI | C15 | C15 | Average duration of an unplanned interruption - water (minutes) | Sydney Water | 129.5 | 22 | 140.9 | 49 | 166.8 | 48 | 140.6 | 48 | 140.2 | 48 | 147.31 | 48 | 154.78 | 48 | 152.63 | 20 | 151 | 93 | 147 | 103 | 136 | 112
NWI | C16 | C16 | Average sewerage interruption (minutes) | Sydney Water | 112 | 22 | 326 | 49 | 246 | 48 | 240 | 48 | 238 | 48 | 239.74 | 48 | 261.23 | 48 | 276.97 | 20 | 277 | 93 | 281 | 103 | 265 | 112
NWI | C17 | C17 | Average frequency of unplanned interruption - water | Sydney Water | - |  | 251.95 | 49 | 221.09 | 48 | 199.61 | 48 | 189.23 | 48 | 175.28 | 48 | 147.2 | 48 | 159.59 | 20 | 183 | 93 | 179 | 103 | 190 | 112 | Data for NWI C17 has been collected from 1 September reports as the database does not allow changes.
NWI | A8 | A8 | Water main breaks (No. per 100km of water main) | Hunter Water | 45 | 22 | 37.4 | 21 | 30.3 | 21 | 32.5798 | 21 | 31.9745 | 21 | 31.1683 | 21 | 25.2331 | 21 | 31.9 | 94 | 30.2 | 94 | 28.9 | 102 | 26.8 | 110
NWI | A10 | A10 | Real losses (L/service connection/d) | Hunter Water | 81 | 22 | 85 | 21 | 80 | 21 | 94 | 21 | 88 | 21 | 84 | 21 | 75 | 21 | 75 | 20 | 82 | 94 | 91 | 102 | 104 | 110
NWI | A14 | A14 | Sewerage mains breaks and chokes (no per 100km sewer main) | Hunter Water | - | 22 | - | 21 | - | 21 | - | 21 | 58.2 | 21 | 59.8 | 21 | 46.5817 | 21 | 42.2754 | 20 | 53.5 | 94 | 53.6 | 102 | 42.7 | 110
NWI | C15 | C15 | Average duration of an unplanned interruption - water (minutes) | Hunter Water | 157 | 22 | 176.6 | 21 | 117.7 | 21 | 120.77 | 21 | 118.6 | 21 | 140.7 | 21 | 121.7 | 21 | 142.4 | 20 | 128 | 94 | 136 | 102 | 137 | 110
NWI | C16 | C16 | Average sewerage interruption (minutes) | Hunter Water | 153 | 22 | 151 | 21 | 144 | 21 | 0 | 21 | 0 | 21 | 141.97 | 21 | 155.9 | 21 | 153.9 | 20 | 148 | 94 | 148 | 102 | 148 | 110
NWI | C17 | C17 | Average frequency of unplanned interruptions - water (no per 1000 properties) | Hunter Water | 387 | 22 | 372 | 21 | 225 | 21 | 271.2387 | 21 | 255.4844 | 21 | 258.4123 | 21 | 205.7461 | 21 | 236.1 | 20 | 303.5 | 94 | 266.6 | 102 | 310.3 | 110 | Hunter Water attributed the increase in unplanned interruptions in 2015-16 to wide variations in soil moisture conditions in HWC’s Area of Operations. Soil conditions were the wettest on record in January 2016 and the driest on record in May 2016.
End of System Continuity and Reliability data
Note on M37: This standard was introduced in 2010/11 however the 2012/13 report provided data for 2008/09 as shown here.
Note on O37: This standard was introduced in 2010/11 however the 2012/13 report provided data for 2009/10 as shown here. Figure corrected in the 2013/14 performance report
Note on M41: This standard was introduced in 2010/11 however the 2012/13 report provided data for 2008/09 as shown here.
Note on O41: This standard was introduced in 2010/11 however the 2012/13 report provided data for 2009/10 as shown here. Figure corrected in the 2013/14 compliance and performance report
Note on O44: This standard commenced in 2010/11 however in the 2013/14 report Hunter Water provided information for the prior year.
Note on M48: This standard was introduced in 2010/11 however the 2012/13 report provided data for 2008/09 as shown here.
Note on O48: This standard was introduced in 2010/11 however the 2012/13 report provided data for 2009/10 as shown here. The data was corrected in the 2013/14 compliance and performance report
Note on Q51: Figure corrected in the 2013/14 Compliance and performance report
Note on K61: Data for Lachlan and Macquarie valleys only.
Note on M61: Data for Lachlan and Macquarie valleys only.
Note on K63: Data for Lachlan and Macquarie valleys only.
Note on O63: Data for Northern valleys only.
Note on U77: Data reported as 'Brogo and Bega', not just 'Bega'.
Note on G83: Responses were all reported as 'immediate'.
Note on K88: The Fish River Water Supply (FRWS) scheme does not yet have daily minimum flow targets. These targets are normally established by DWE as part of a Water Sharing Plan. The Fish River does not yet have a Water Sharing Plan and State Water is not aware of any plans by DWE to develop such a plan. In previous reports, State Water has interpreted this requirement as an average riparian release of 1.9 ML per day. In response to the severity of the drought, in 2007/08 State Water sought and received approval from DWE for releases to the Fish River to mimic natural flow release variations. In addition, during 2007/08 the scheme maintained water restrictions, with the approval of with the FRWS Customer Council.
Note on M88: The Fish River Water Supply (FRWS) scheme does not yet have daily minimum flow targets. These targets are normally established by NOW (formerly DWE) as part of a WSP. The Fish River does not yet have a WSP and State Water is not aware of any plans by NOW to develop such a plan. In previous reports, State Water has interpreted this requirement as an average riparian release of 1.9 ML per day. In response to the severity of the drought, in 2007/08 State Water sought and received approval from the then DWE for releases to the Fish River to mimic natural flow release variations. In addition, during 2007/08 the scheme maintained water restrictions, with the approval of with the FRWS Customer Council.
Note on O88: The Fish River Water Supply (FRWS) scheme does not yet have daily minimum flow targets. These targets are normally established by NOW (formerly DWE) as part of a WSP. The Fish River does not yet have a WSP and State Water is not aware of any plans by NOW to develop such a plan. In previous reports, State Water has interpreted this requirement as an average riparian release of 1.9 ML per day. In response to the severity of the drought, in 2007/08 State Water sought and received approval from the then DWE for releases to the Fish River to mimic natural flow release variations. In addition, during 2007/08 the scheme maintained water restrictions, with the approval of with the FRWS Customer Council.
Note on Q88: The Fish River Water Supply (FRWS) scheme does not yet have daily minimum flow targets. These targets are normally established by NOW as part of a WSP. The Fish River does not yet have a WSP. In relation to Oberon Dam in previous reports, State Water has interpreted this requirement as an average riparian release of 1.ML per day from the dam. In relation to accessing water from Duckmaloi River State Water has interpreted this requirement as maintaining a minimum flow of 6ML per day downstream of the Duckmaloi Weir. Consequent to the Minister's review of water sharing arrangements in the FRWS, this minimum flow requirements has been reduced to 3ML per day and this was effective from 7 March 2011. There were only 3 days in 2010-2011 when this minimum flow requirements had not been met, resulting in 99% compliance.
Note on S93: IPART: revised from 48 to 49 for 2014-15 reporting period. See 103
Note on G96: Data in spreadsheet unreliable for 2005/06 NWI C17. Indicator not reported in 1 September report.

## SC&R Appendix
TABLE 1 | Indicator I3 (2006/07) - Hunter Water detail of events where 250 or more properties were affected in a single event by either a planned or an unplanned water interruption either of which is longer than 5 hrs.
Job No | Date of Interruption | Location |  | No. Properties | Duration (hr)
223896 | 2006-09-28 | BEACH RD, WANGI WANGI |  | 258 | 6.9
Various elevated areas in Wangi were affected due to a 200m water main failure off Summerhill Rd, Wangi
228123 | 2006-11-24 | CORMORANT ST, KOORAGANG |  | 1995 | 13.5
Various areas in Stockton and Fern Bay were affected due to a 500mm water main failure at the intersection of Comorant and Greenleaf Rd, Kooragang. This main is the only supply to the Stockton & Fern Bay area. Hunter Water has approved the expenditure of $1M to mitigate this risk in the future with additional new pipework to be installed by late 2007
234991 | 2007-01-23 | BOWMAN ST, SWANSEA |  | 531 | 3.5-8.5
Various areas in Swansea and Caves Beach were affected for approximately 3 - 8 hrs depending on elevation due to a 200 mm water main failure at Bowman St, Swansea.
247284 | 2007-06-06 | EXCELSIOR ST, TORONTO |  | 840 | 6.7-8.1
Various areas in Toronto affected for approximately 6 - 8 hrs depending on elevation due to a 250mm waterman failure at Excelsior Pd, Toronto. At the time of the break, Coal point Peninsula was relying on Toronto No. 3 Reservoir for supply as Coal Point No. 2 Reservoir was offline for scheduled maintenance.
247620 | 2007-06-08 | Various ST, VALENTINE |  | 494 | 5.2
Major Storm June 2007 - All properties in Valentine Water Pumping Station Zone were affected due to power failure at the pumping station during the storm.
247598 | 2007-06-08 | Various ST, CARDIFF HEIGHTS |  | 823 | 11.4
Major Storm June 2007 - All properties in Christina St High Level Zone were affected due to the power failure at Cardiff (Murray St) Water Pumping Station during the storm.
247564 | 2007-06-09 | Various ST, MAQUARIE HILLS |  | 741 | 12
Major Storm June 2007 - All properties in Macquarie St High Level at Macquarie Hills Water Pumping Station during the storm.
247623 | 2007-06-09 | Various ST, TORONTO |  | 3683 | 7.7
Major Storm 2007 - All properties in Toronto No. 2 reservoir zone were affected due to power failure at Toronto Water pumping station during the storm.
Source: | Reference # | 59 | pg 5 | Hunter Water System Performance Schedule 4 2006-07 Report to IPART August 2007
TABLE 2 | Indicator I3 (2010/11) - Hunter Water Events leading to a planned or unplanned water interruption where 250 or more properties experience an interruption of over five hours duration.
Job No | Date of interruption | Location - Street, suburb |  | No. Properties | Duration (hrs) | Comments
32266 | 2010-07-08 | Mount Hall Rd | Raymond Terrace | 254 | 6.3 | 375mm main damaged by external party
338411 | 2010-09-22 | Comorant Dr | Kooragang Island | 2120 | 6.1 | Water break on 200mm main
359057 | 2011-06-15 | Secret Corner | Rathmines | 468 | 6.2 | Failure of new connection on 200mm main
356278 | 2011-05-16 | Newcastle Rd | Wallsend | 399 | 5.7 | Leak on contract connection on 500mm main in Water Pumping Station
358092 | 2011-06-23 | Main Rd | Glendale | 630 | 5.9 | Complication caused by installation of flowmeter on 500mm main
Source: | Reference # | 56 | pg 12 | Hunter Water Service Quality and System Performance Report 2010-11
TABLE 3 | Indicator I3 (2011/12) - Hunter Water Events leading to a planned or unplanned water interruption where 250 or more properties experience an interruption of over five hours duration.
Job No | Date of interruption | Location - Street, suburb |  | No. Properties | Duration (hrs) | Comments | Interruption type
359993 | 2011-07-04 | All streets | Boat Harbour | 399 | 5.9 | Air scouring | Planned
360624 | 2011-07-01 | Various streets | Coal Point | 311 | 5.3 | Air scouring | Planned
375382 | 2011-12-01 | Faul St | Adamstown Heights | 398 | 5.5 | 200mm main break | Unplanned
379964 | 2012-02-16 | High St | The Hill | 306 | 5.5 | Replace stop valves | Unplanned
Source: | Reference # | 57 | pg 12 | Hunter Water Service Quality and System Performance Report 2011-12
TABLE 4 | Indicator I3 (2012/13) - Hunter Water Events leading to a planned or unplanned water interruption where 250 or more properties experience an interruption of over five hours duration.
Job No | Date of interruption | Location - Street, suburb |  | No. Properties | Duration (hrs) | Comments | Interruption type
392208 | 2012-07-20 | Thalab Road | New Lambton | 309 | 5.9 | 200mm break | Unplanned
394250 | 2012-11-02 | Various streets | Fletcher/Wallsend | 2008 | 7.2–15.3 | 500mm break | Unplanned
403617 | 2012-03-01 | Adelaide Street | Raymond Terrace | 660 | 6.1 | 250mm break | Unplanned
Source: | Reference # | 63 | pg 120 | Hunter Water Corporation Compliance and Performance Report 2012-13
TABLE 5 | Indicator I3 (2013/14) - Hunter Water Events leading to a planned or unplanned water interruption where 250 or more properties experience an interruption of over five hours duration.
Job No | Date of interruption | Location - Street, suburb |  | No. Properties | Duration (hrs) | Comments | Interruption type
427980 | 2013-10-19 | Ellalong Rd | Pelton | 498 | 5.3 | 250mm break | Unplanned
435455 | 2014-04-22 | Various streets | Wangi | 494 | 10.4 | 600mm break | Unplanned
Source | Reference # | 94 | pg 132 | Hunter Water Corporation Compliance and Performance Report 2013-2014
End of System Continuity and Reliability Appendix

## Environmental Performance
Chapter 3: Environmental Performance
Indicator/System Performance Standard |  |  |  | Utility | 2005/06 |  | 2006/07 |  | 2007/08 |  | 2008/09 |  | 2009/10 |  | 2010/11 |  | 2011/12 |  | 2012/13 |  | 2013/14 |  | 2014/15 |  | 2015/16 |  | Notes/Comments
Type | NEW No. | Prev. No. | Description
IPART | WC1 | WC1 | The quantity of potable water that Sydney Water has drawn from all sources in the preceding financial year (L/person/day) | Sydney Water | 341 | 25 | 328 | 27 | 306 | 39 | 309 | 30 | 315 | 41 | 303 | 43 | 286 | 51 | 305 | 44 | 310 | 92 | 294 | 104 | 297 | 114
|  |  | Licence Standard | Sydney Water | - |  | - |  | - |  | - |  | - |  | 329 |  | 329 |  | 329 |  | 329 |  | 329 |  | 329
IPART | WC1 | WC1 | The weather corrected quantity of potable water that Sydney Water has drawn from all sources in the preceding financial year (L/person/day) | Sydney Water | 335.2 | 75 | 326.3 | 75 | 308 | 75 | 310 | 75 | 309 | 75 | 304 | 75 | 297 | 75 | 310 | 75 | 307 | 92 | 295 | 104 | 293 | 114
|  |  | Licence Standard | Sydney Water | - |  | - |  | - |  | - |  | - |  | 329 |  | 329 |  | 329 |  | 329 |  | 329 |  | 329
IPART | WC2 | WC2 | The amount of water leakage from the Drinking Water Supply System, averaged for the preceding financial year (ML/day) | Sydney Water | 123 | 25 | 121 | 27 | 117 | 39 | 105 | 30 | 96.775 | 47 | 106 | 43 | 115 | 55 | 120 | 69 | 107 | 92 | 99 | 104 | 103 | 114
|  |  | Water leakage level (ML/day) | Sydney Water | - |  | - |  | - |  | 105±16 |  | 105±16 |  | 105±16 |  | 105±16 |  | 105±16 |  | 105±16 |  | 105±16 |  | 105±16
IPART | E1 | E1 | Total number of proceedings and Penalty Notices under the Protection of the Environment Operations (POEO)Act 1997 issued to the water utility | Sydney Water | 3 | 24 | 2 | 27 | 0 | 30 | 1 | 30 | 0 | 41 | 2 | 42 | 0 | 45 | 1 | 64 | 4 | 96 | 2 | 105 | 2 | 111
IPART | E2 | E2 | Total number of proceedings and Penalty Notices under the Protection of the Environment Operations (POEO) Act 1997 issued to contractors engaged by the water utility. | Sydney Water | 0 | 24 | 0 | 27 | 1 | 30 | 1 | 30 | 1 | 41 | 1 | 42 | 1 | 45 | 1 | 64 | 0 | 96 | 0 | 105 | 0 | 111
IPART | E3 | E3 | Total electricity consumption by water assets (kWh/ML of water supplied to be included). | Sydney Water | 267.22 | 24 | 283.32 | 27 | 273.2 | 45 | 275.9 | 45 | 283.7 | 45 | 271.7 | 45 | 274 | 45 | 275.1 | 64 | 279.9 | 96 | 268.9 | 105 | 277.3 | 111
IPART | E4 | E4 | Total electricity consumption by sewer assets (KWh/ML of sewage collected) | Sydney Water | 496.49 | 24 | 467.58 | 27 | 426.7 | 45 | 485.3 | 45 | 484.8 | 45 | 459.6 | 45 | 429.4 | 45 | 470.1 | 64 | 492.1 | 96 | 461.5 | 105 | 429.6 | 111
IPART | E5 | E5 | Electricity consumption from renewable sources or generated by the water utility expressed as a percentage of total electricity consumption | Sydney Water | 6.8% | 24 | 6.1% | 27 | 4.9% | 45 | 6.3% | 45 | 10.3% | 45 | 14.6% | 45 | 16.6% | 45 | 16.2% | 64 | 16% | 96 | 17.5% | 105 | 21% | 111
IPART | - | E6 (S) | Total number of Controlled Sewage Overflows that occur in dry weather | Sydney Water | 45 | 24 | 34 | 27 | 19 | 30 | 13 | 30 | 12 | 41 | 25 | 42 | 11 | 45 | 15 | 64
IPART | - | E7 (S) | Total volume of Controlled Sewage Overflows that occur in wet weather (ML) | Sydney Water | 3700 | 24 | 32400 | 27 | 21000 | 30 | 4900 | 30 | 6500 | 41 | 5350 | 42 | 22471 | 45 | 13858 | 64
IPART | - | E8 (S) | Licence Standard (% responded to within 6 hours) | Sydney Water | 18 | 24 | 25 | 27 | 28 | 30 | 27 | 30 | 22 | 41 | 29 | 42 | 30 | 45 | 21 | 64
IPART | E6 (S) | E9 (S) | Total volume of Controlled Sewage Overflows that occur in dry weather, expressed as a percentage of total sewage effluent discharged to the environment | Sydney Water | 0.001% | 24 | 0.001% | 27 | 0.001% | 30 | 0.001% | 30 | <0.001% | 41 | <0.001% | 42 | <0.001% | 45 | 0.001% | 64 | 0.001% | 96 | 0.002% | 105 | 0.002% | 111
IPART | E7 | E10 (S) | Percentage of trade waste customers in compliance with their wastewater discharge limits as outlined in their water utility trade waste agreements | Sydney Water | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92% | 64 | 95.2% | 96 | 97.5% | 105 | 97% | 111
IPART | E8 | E11 | Total mass of bio solids produced by the water utility (dry tonnes) | Sydney Water | 50489 | 24 | 52149 | 27 | 42564 | 45 | 39443 | 45 | 38114 | 45 | 38074 | 45 | 40592 | 64 | 39939 | 64 | 37118 | 96 | 40627 | 105 | 39370 | 111
IPART | E9 | E12 | Percent of solid waste recycled or reused expressed as a percentage of solid waste generated | Sydney Water | 95% | 24 | 97% | 27 | 86% | 45 | 53% | 45 | 74% | 45 | 72% | 45 | 72% | 45 | 57% | 64 | 88% | 96 | 88% | 105 | 71% | 111
IPART | E10 | E13 (S) | Total mass of solid waste generated by the water utility (tonnes) | Sydney Water | 460779 | 24 | 428846 | 27 | 499572 | 45 | 481524 | 45 | 361733 | 45 | 224642 | 45 | 214875 | 45 | 144401 | 64 | 196137 | 96 | 329055 | 105 | 190230 | 111
IPART | E11 | E14 | Total area of clearing of native vegetation (ha). | Sydney Water | 1.37 | 75 | 0.9 | 75 | 3.89 | 75 | 3.14 | 75 | 5.44 | 75 | 1.8 | 75 | 4 | 75 | 0.02 | 64 | 7.94 | 96 | 7.99 | 105 | 2.92 | 111
IPART | E12 | E15 | Total area of native vegetation rehabilitated (ha). | Sydney Water | 0.83 | 75 | 1.3 | 75 | 2.08 | 75 | 4.55 | 75 | 30.12 | 75 | 2.2 | 75 | 2.3 | 75 | 3.9 | 64 | 7.38 | 96 | 19.03 | 105 | 6.23 | 111
IPART | E13 | E16 (S) | Total area of native vegetation gain due to rehabilitation, replanting and protection by Sydney Water. | Sydney Water | -0.54 | 75 | 0.4 | 75 | -1.81 | 75 | 1.41 | 75 | 24.68 | 75 | 0.4 | 75 | -1.7 | 75 | 3.88 | 64 | -0.56 | 96 | 11.04 | 105 | 3.31 | 111
IPART | E14 | E17 | Total number and nature of proceedings or Penalty Notices of conditions under licences issued to the water utility by NOW for water management | Sydney Water | - |  | - |  | - |  | - |  | - |  | - |  | - |  | 0 | 64 | 0 | 96 | 0 | 105 | 0 | 111
IPART | 3.1.1 | 3.1.1 | Five year rolling average for annual residential water consumption calculated for each financial year | Hunter Water | - |  | - |  | 196 | 35 | 191 | 35 | 188 | 35 | 182 | 61 | 176 | 62 | 175.5 | 63 | 176 | 94 | 173 | 102 | 171 | 110
|  |  | Licence Standard (no more than 215kL/property/yr) | Hunter Water | - |  | - |  | 215 |  | 215 |  | 215 |  | 215 |  | 215 |  | 215 |  | 215 |  | 215 |  | 215
IPART | E1 | E1 | Total number of proceedings and Penalty Notices under the Protection of the Environment Operations (POEO) Act 1997 issued to the water utility. | Hunter Water | - |  | - |  | 1 | 35 | 0 | 35 | 1 | 35 | 0 | 61 | 0 | 63 | 2 | 63 | 0 | 94 | 1 | 102 | 1 | 110
IPART | E2 | E2 | Total number of proceedings and Penalty Notices under the Protection of the Environment Operations (POEO) Act 1997 issued to contractors engaged by the water utility | Hunter Water | - |  | - |  | 0 | 35 | 0 | 35 | 0 | 35 | 0 | 61 | 0 | 62 | 0 | 63 | 1 | 94 | 0 | 102 | 0 | 110
IPART | E3 | E3 | Total electricity consumption by water assets (kWh/ML of water supplied to be included). | Hunter Water | - |  | - |  | 473 | 35 | 561 | 63 | 503 | 35 | 498 | 61 | 456 | 62 | 435 | 63 | 430 | 94 | 461 | 102 | 452 | 110 | Hunter Water revised historical data for 2008/09 to accurately reflect the information available. Reference #91 provides details of this revision.
IPART | E4 | E4 | Total electricity consumption by sewer assets (KWh/ML of sewage collected). | Hunter Water | - |  | - |  | - |  | 667 | 63 | 673 | 63 | 612 | 63 | 559 | 63 | 624 | 63 | 672 | 94 | 584 | 102 | 626 | 110
IPART | E5 | E5 | Electricity consumption from renewable sources or generated by the water utility expressed as a percentage of total electricity consumption. | Hunter Water | - |  | - |  | - |  | - |  | 0 | 35 | 0 | 61 | 0 | 62 | 0.03% | 63 | 0.29% | 94 | 0.6% | 102 | 0.33% | 110 | During 2013-14, a cogeneration facility was commissioned at Cessnock Wastewater Treatment Works to generate electricity from digester biogas.
IPART | E6 | E11 | Total mass of bio solids produced by the water utility. (kg) | Hunter Water | - |  | - |  | - |  | 5762 | 63 | 4920 | 63 | 4911 | 63 | 5532 | 63 | 5778 | 63 | 5988 | 94 | 6032 | 102 | 7397 | 110
IPART | E7 | E12 | Percent of solid waste recycled or reused expressed as a percentage of solid waste generated. | Hunter Water | - |  | - |  | 88% | 60 | 84% | 63 | 92.5% | 76 | 94.7% | 61 | 90.5% | 62 | 87% | 63 | 69% | 94 | 86% | 102 | 78% | 110
IPART | E8 | - | Total area of clearing of native vegetation (ha). | Hunter Water | [16 empty] | 0.56 | 94 | 3.3 | 102 | 19.8 | 110 | New indicator implemented from 2013/14 Hunter Water attributed the increase in 2015/16 to widening of the cleared corridors for overhead power lines to reduce bushfire risk.
IPART | E9 | - | Total area of native vegetation rehabilitated (ha). | Hunter Water | [16 empty] | 160.1 | 94 | 0 | 102 | 8.7 | 110 | New indicator implemented from 2013/14
IPART | E10 | - | Total area of native vegetation gain due to rehabilitation, replanting and protection by Hunter Water. | Hunter Water | [16 empty] | 159.5 | 94 | -3.3 | 102 | -11.2 | 110 | New indicator implemented from 2013/14
IPART | E11 | E17 | Total number and nature of proceedings or Penalty Notices of conditions under licences issued to the water utility by NOW for water management. | Hunter Water | [6 empty] | 0 | 63 | 0 | 63 | 0 | 63 | 0 | 63 | 0 | 63 | 0 | 94 | 0 | 102 | 0 | 110 | Whilst there have historically been breaches, these have not resulted in proceedings or penalty notices being issued.
|  |  | Total number | Hunter Water | [6 empty] | 0 | 63 | 0 | 63 | 0 | 63 | 0 | 63 | 0 | 63 | 0 |  | 0 |  | 0 | 110
|  |  | Nature | Hunter Water | [6 empty] | N/A | 63 | N/A | 63 | N/A | 63 | N/A | 63 | N/A | 63 | N/A |  | N/A |  | N/A | 110
IPART | BH-B-M | BH-B-M | 2001 and 2006 spring ausRivAS scores, plus additional data from sustainable rivers audit (SRA) | WaterNSW(SCA) | Chapter 5.2 | 73 |  |  | Chapter 6.2 | 72 |  |  |  |  | Chapter 4.1 | 71 |  |  | Chapter 6.7 | 70 | [6 empty] | Catchment audits are not undertaken on an annual basis.
IPART | WA-SW-SWF | WA-SW-SWF | Level and variability of streamflow | WaterNSW(SCA) | Chapter 3.1 | 73 |  |  | Chapter 4.1 | 72 |  |  |  |  | Chapter 5.1 | 71 |  |  | Chapter 4.1 | 70 | [6 empty] | Catchment audits are not undertaken on an annual basis.
IPART | WA-SW-EF | WA-SW-EF | total volume of water by type released from SCA storages - ENVIRONMENTAL FLOWS | WaterNSW(SCA) | Chapter 3.3 | 73 |  |  | Chapter 4.3 | 72 |  |  |  |  | Chapter 5.2 | 71 |  |  | Chapter 4.2 | 70 | [6 empty] | Catchment audits are not undertaken on an annual basis.
NWI | W1 | W1 | Volume of water sourced from surface water (ML) | Sydney Water | - | - | 6395 | 49 | 5486 | 48 | 5885 | 66 | 6065 | 66 | 5589 | 66 | 5141 | 66 | 6395 | 66 | 6862 | 93 | 6468 | 103 | 5955 | 112
NWI | W2 | W2 | Volume of water sourced from groundwater (ML) | Sydney Water | - | - | 0 | 49 | - | 48 | N/A | 66 | N/A | 66 | N/A | 66 | N/A | 66 | N/A | 66 | N/A | 93 | N/A | 103 | N/A | 112
NWI | W3 | W3 | Volume of water sourced from desalination (ML) | Sydney Water | - | - | 0 | 49 | 0 | 48 | 0 | 66 | 19952 | 66 | 77102 | 66 | 61290 | 66 | 0 | 66 | 0 | 93 | 0 | 103 | 0 | 112
NWI | W4 | W4 | Volume of water sourced from recycling (ML) | Sydney Water | - | - | 20999 | 75 | 23531 | 75 | 22408 | 66 | 28040 | 66 | 42322 | 66 | 40742 | 66 | 41776 | 66 | 41543 | 93 | 38280 | 103 | 38465 | 112
NWI | W5 | W5 | Volume of water received from bulk supplier (ML) | Sydney Water | - | - | 502692 | 49 | 475156 | 48 | 491727 | 66 | 479633 | 66 | 414004 | 66 | 415498 | 66 | 510299 | 66 | 523725 | 93 | 509573 | 103 | 528687 | 112 | This volume is supplied by SCA who sources its water from surface water.
NWI | W6 | W6 | Volume of bulk recycled water purchased (ML) | Sydney Water | - | - | 0 | 49 | - | 48 | N/A | 66 | N/A | 66 | N/A | 66 | N/A | 66 | N/A | 66 | N/A | 93 | N/A | 103 | N/A | 112
NWI | W7 | W7 | Total sourced water (ML) | Sydney Water | - | - | 530086 | 75 | 504173 | 75 | 520020 | 75 | 533690 | 66 | 539017 | 66 | 522671 | 66 | 558470 | 66 | 572129 | 93 | 554321 | 103 | 573107 | 112
NWI | W8 | W8 | Volume of water supplied – residential (ML) | Sydney Water | - | - | 316813 | 49 | 292782 | 48 | 320861 | 66 | 334488 | 66 | 324053 | 66 | 323953 | 66 | 335976 | 66 | 354877 | 93 | 352843 | 103 | 356577 | 112 | Sydney Water has revised the data in 2014-15 reporting period for 2011-12 and 2010-11 as a result of error made in historical calculations
NWI | W9 | W9 | Volume of water supplied – Commercial, municipal and industrial (ML) | Sydney Water | - | - | 147644 | 49 | 136064 | 48 | 126712 | 66 | 130640 | 66 | 127443 | 66 | 119496 | 93 | 123842 | 93 | 126539 | 93 | 123680 | 103 | 130673 | 112 | Sydney Water has revised the data in the 2014-15 reporting period for 2012-13, 2011-12 and 2010-11 as a result of error made in historical calculations
NWI | W10 | W10 | Volume of water supplied – other (ML) | Sydney Water | - | - | 45473 | 49 | 52855 | 48 | 44395 | 66 | 50268 | 66 | 54827 | 66 | 49158 | 66 | 63729 | 93 | 60076 | 93 | 52302 | 103 | 51654 | 112
NWI | W18 | W18 | Total sewage collected (ML) | Sydney Water | - | - | 485512 | 49 | 546381 | 48 | 475692 | 66 | 464237 | 66 | 509435 | 66 | 588097 | 66 | 496575 | 66 | 469579 | 93 | 564424 | 103 | 547783 | 112
NWI | W19 | W19 | Sewage collected per property (kL/property) | Sydney Water | - | - | 290 | 49 | 324 | 48 | 279 | 66 | 269 | 66 | 292 | 66 | 334 | 66 | 277 | 66 | 261 | 93 | 309 | 103 | 296 | 112
NWI | W20 | W20 | Volume of recycled water supplied -Residential (ML) | Sydney Water | - | - | 1652 | 49 | 1402 | 48 | 1704 | 66 | 2209 | 66 | 2250 | 66 | 1873 | 66 | 2064 | 66 | 2137 | 93 | 2138 | 103 | 2489 | 112
NWI | W21 | W21 | Volume of recycled water supplied –Commercial, municipal and industrial (ML) | Sydney Water | - | - | 5995 | 49 | 7212 | 48 | 5155 | 66 | 7537 | 66 | 7687 | 66 | 9683 | 66 | 10544 | 66 | 10205 | 93 | 9682 | 103 | 9899 | 112
NWI | W22 | W22 | Volume of recycled water supplied -Agricultural (ML) | Sydney Water | - | - | 130 | 49 | 632 | 48 | 3034 | 66 | 5643 | 66 | 5199 | 66 | 5187 | 66 | 5175 | 66 | 5400 | 93 | 4795 | 103 | 4876 | 112
NWI | W23 | W23 | Volume of recycled water supplied –Environmental (ML) | Sydney Water | - | - | 0 | 49 | 0 | 48 | 0 | 66 | 1980 | 66 | 15989 | 66 | 13362 | 66 | 15142 | 66 | 14990 | 93 | 11779 | 103 | 10837 | 112
NWI | W24 | W24 | Volume of recycled water supplied – On site (ML) | Sydney Water | - | - | 13352 | 49 | 14917 | 48 | 15549 | 66 | 16314 | 66 | 16396 | 66 | 15823 | 66 | 14026 | 66 | 14211 | 93 | 14680 | 103 | 15241 | 112
NWI | E1 | E1 | Percent of sewage treated to a primary level | Sydney Water | - | - | - | - | 67.06% | 23 | 74.27% | 75 | 75.7% | 75 | 75% | 101 | 73% | 101 | 74% | 101 | 74.2% | 96 | 73.1% | 105 | 73.3% | 111
NWI | E2 | E2 | Percent of sewage treated to a secondary level | Sydney Water | - | - | - | - | 10.53% | 23 | 3.268% | 75 | 3.205% | 75 | 3.428% | 101 | 4% | 101 | 4% | 101 | 3.3% | 96 | 4.2% | 105 | 4.1% | 111
NWI | E3 | E3 | Percent of sewage treated to a tertiary or advanced level | Sydney Water | - | - | - | - | 22.35% | 23 | 22.37% | 75 | 21.02% | 75 | 20.99% | 101 | 23% | 101 | 22% | 101 | 22.5% | 96 | 22.7% | 105 | 22.6% | 111
NWI | E8 | E8 | Percent of bio solids reused | Sydney Water | - | - | 100% | 42 | 100% | 45 | 100% | 45 | 100% | 45 | 100% | 45 | 100% | 45 | 100% | 64 | 100% | 96 | 100% | 105 | 100% | 111
NWI | W1 | W1 | Volume of water sourced from surface water (ML) | Hunter Water | 60934 | 22 | 63711 | 22 | 64311 | 22 | 61814 | 63 | 63433 | 63 | 65676 | 63 | 61035 | 63 | 66060 | 63 | 67253 | 94 | 64281 | 102 | 59444 | 110
NWI | W2 | W2 | Volume of water sourced from groundwater (ML) | Hunter Water | 1971 | 22 | 11158 | 22 | 3025 | 22 | 5504 | 63 | 7117 | 63 | 2333 | 63 | 2159 | 63 | 2561 | 63 | 4230 | 94 | 2734 | 102 | 9016 | 110 | Hunter Water stated that the large increase in 2015-16 is a result of Tomago source water being treated at Grahamstown Water Treatment Plant for a period of two months. This partial source substitution was undertaken in response to a moderate increase in blue-green algae concentrations in Grahamstown Dam at the time.
NWI | W3 | W3 | Volume of water sourced from desalination (ML) | Hunter Water | - | 22 | - | 22 | - | 22 | - | 63 | - | 63 | 0 | 63 | 0 | 63 | 0 | 63 | 0 | 120 | 0 | 102 | 0 | 110
NWI | W4 | W4 | Volume of water sourced from recycling (ML) | Hunter Water | 1860 | 22 | 2055 | 22 | 2174 | 22 | 2872 | 63 | 2899 | 63 | 2186 | 63 | 1873 | 63 | 1874 | 63 | 2505 | 94 | 3045 | 102 | 4292 | 110
NWI | W5 | W5 | Volume of water received from bulk supplier (ML) | Hunter Water | - | 22 | - | 22 | - | 22 | - | 63 | - | 63 | 0 | 63 | 0 | 63 | 0 | 63 | 267 | 94 | 257 | 102 | 321 | 110
NWI | W6 | W6 | Volume of bulk recycled water purchased (ML) | Hunter Water | 0 | 22 | 0 | 22 | 0 | 22 | 0 | 63 | 0 | 63 | 0 | 63 | 0 | 63 | 0 | 63 | 0 | 94 | 0 | 102 | 0 | 110
NWI | W7 | W7 | Total sourced water (ML) | Hunter Water | 74765 | 22 | 76924 | 22 | 69510 | 22 | 70190 | 63 | 73449 | 63 | 70195 | 63 | 65067 | 63 | 70495 | 63 | 74255 | 94 | 70317 | 102 | 73073 | 110
NWI | W8 | W8 | Volume of water supplied – residential (ML) | Hunter Water | 40553 | 22 | 39238 | 22 | 36428 | 22 | 37199 | 63 | 38463 | 63 | 37087 | 63 | 34911 | 63 | 38370 | 63 | 40150 | 94 | 37723 | 102 | 37936 | 110
NWI | W9 | W9 | Volume of water supplied – Commercial, municipal and industrial (ML) | Hunter Water | 20784 | 22 | 22027 | 22 | 20866 | 22 | 21487 | 63 | 21081 | 63 | 21068 | 63 | 20923 | 63 | 22670 | 63 | 23580 | 94 | 21430 | 102 | 22277 | 110
NWI | W10 | W10 | Volume of water supplied – other (ML) | Hunter Water | 8538 | 22 | 9334 | 22 | 8715 | 22 | 8334 | 63 | 8689 | 63 | 9539 | 63 | 9226 | 63 | 9198 | 63 | 9995 | 94 | 10596 | 102 | 12189 | 110
NWI | W18 | W18 | Total sewage collected (ML) | Hunter Water | 59918 | 22 | 76338 | 22 | 74383 | 22 | 64815 | 63 | 55481 | 63 | 67869 | 63 | 80777 | 63 | 68097 | 63 | 64878 | 94 | 71838 | 102 | 70208 | 110
NWI | W19 | W19 | Sewage collected per property (kL/property) | Hunter Water | 296 | 22 | 372 | 22 | 356 | 22 | 307.2 | 63 | 260.5 | 63 | 314.2 | 63 | 368.9 | 63 | 307.5 | 63 | 289.2 | 94 | 315.8 | 102 | 304.4 | 110
NWI | W20 | W20 | Volume of recycled water supplied - Residential (ML) | Hunter Water | 0 | 22 | 0 | 22 | 0 | 22 | 0 | 63 | 0 | 63 | 0 | 63 | 0 | 63 | 0 | 63 | 0 | 94 | 0 | 102 | 0 | 110
NWI | W21 | W21 | Volume of recycled water supplied – Commercial, municipal and industrial (ML) | Hunter Water | 1686 | 22 | 1875 | 22 | 1984 | 22 | 2289 | 63 | 2648 | 63 | 2006 | 63 | 1643 | 63 | 1644 | 63 | 2274 | 94 | 2858 | 102 | 4106 | 110
NWI | W22 | W22 | Volume of recycled water supplied - Agricultural (ML) | Hunter Water | 2040 | 22 | 1967 | 22 | 2269 | 22 | 2623 | 63 | 2520 | 63 | 2488 | 63 | 2824 | 63 | 2445 | 63 | 2441 | 94 | 1562 | 102 | 1087 | 110
NWI | W23 | W23 | Volume of recycled water supplied – Environmental (ML) | Hunter Water | 0 | 22 | 0 | 22 | 0 | 22 | 0 | 63 | 0 | 63 | 0 | 63 | 0 | 63 | 0 | 63 | 0 | 94 | 0 | 102 | 0 | 110
NWI | W24 | W24 | Volume of recycled water supplied – On site (ML) | Hunter Water | 216 | 22 | 218 | 22 | 218 | 22 | 180 | 63 | 180 | 63 | 180 | 63 | 198 | 63 | 180 | 63 | 180 | 94 | 180 | 102 | 180 | 110
NWI | E1 | E1 | Percent of sewage treated to a primary level | Hunter Water | 0% | 22 | 0% | 22 | 0% | 22 | - | 63 | - | 63 | - | 63 | - | 63 | - | 63 | 0% | 94 | 0% | 102 | 0% | 110
NWI | E2 | E2 | Percent of sewage treated to a secondary level | Hunter Water | 54% | 22 | 56% | 22 | 56% | 22 | 57.8% | 63 | 59.1% | 63 | 54.4% | 63 | 56.1% | 63 | 55.7% | 63 | 56.5% | 94 | 72.2% | 102 | 73.9% | 110
NWI | E3 | E3 | Percent of sewage treated to a tertiary or advanced level | Hunter Water | 46% | 22 | 44% | 22 | 44% | 22 | 42.2% | 63 | 41% | 63 | 45.6% | 63 | 44% | 63 | 44.3% | 63 | 43.4% | 94 | 27.8% | 120 | 26.1% | 110 | The interpretation of this indicator changed in 2014/15 so it is not comparable to previous historical data.
NWI | E8 | E8 | Percent of bio solids reused | Hunter Water | 88% | 22 | 104% | 22 | 100% | 22 | 88% | 63 | 104% | 63 | 95% | 63 | 86% | 63 | 92% | 63 | 85% | 94 | 89% | 102 | 88% | 110
NWI | W1 | W1 | Volume of water sourced from surface water (ML) | WaterNSW(SCA) | 524316 | 22 | 503693 | 22 | 478184 | 20 | 490283 | 20 | 582623 | 20 | 736650 | 20 | 880572 | 20 | 847623 | 20 | 824365 | 100 | 888144 | 107 | 924337 | 115
NWI | W2 | W2 | Volume of water sourced from groundwater (ML) | WaterNSW(SCA) | - | 22 | 450 | 22 | 169 | 20 | 0 | 20 | 0 | 20 | 0 | 20 | 0 | 20 | 0 | 20 | 0 | 100 | 0 | 107 | 0 | 115
NWI | W5 | W5 | Volume of water received from bulk supplier (ML) | WaterNSW(SCA) | 2098 | 22 | 3115 | 22 | 1077 | 20 | 208 | 20 | 0 | 20 | 224 | 20 | 25 | 20 | 1014 | 20 | 2524 | 100 | 2043 | 107 | 2181 | 115
NWI | W5.2 | W5.2 | Volume of non-potable water received from bulk supplier (ML) | WaterNSW(SCA) | [18 empty] | 2043 | 115 | 2181 | 115
NWI | W7 | W7 | Total sourced water (ML) | WaterNSW(SCA) | 526414 | 22 | 507258 | 22 | 479430 | 20 | 490491 | 20 | 582623 | 20 | 736874 | 20 | 880597 | 20 | 848637 | 20 | 826889 | 100 | 890187 | 107 | 926518 | 115
NWI | W11 | W11 | Total urban water supplied | WaterNSW(SCA) | - | 22 | - | 22 | - | 20 | - | 20 | - | 20 | 433363 | 20 | 432443 | 20 | 536949 | 20 | 551686 | 100 | 538472 | 107 | 555110 | 115
NWI | W11.2 | W11.2 | Total urban non-potable water supplied | WaterNSW(SCA) | [18 empty] | 538472 | 115 | 555110 | 115
NWI | W13 | W13 | Total volume of water supplied - Environmental (ML) | WaterNSW(SCA) | 64495 | 22 | 70156 | 22 | 70842 | 20 | 80680 | 20 | 82382 | 20 | 293085 | 20 | 440325 | 20 | 310309 | 20 | 272314 | 100 | 349307 | 107 | 368861 | 115
NWI | W14 | W14 | Volume of bulk water exports (ML) | WaterNSW(SCA) | [18 empty] | 520830 | 115 | 535091 | 115
NWI | W14.2 | W14.2 | Volume of non-potable bulk water exports | WaterNSW(SCA) | [18 empty] | 520830 | 115 | 535091 | 115
End of Environmental Performance data
Note on A2: ~!Print_TitlesºXFD4 =.
Note on C5: = D5# =.
Note on U11: In 2012/13 the wording for this indicator changed slightly to exclude clean-up notices.
Note on C30: = D30# =.
Note on C43: = D43# =.
Note on G46: Data in spreadsheet unreliable for 2005/06 NWI W1.
Note on Q53: IPART: Data revised in 2014-15. See notes
Note on S53: IPART: Data revised in 2014-15. See notes
Note on Q54: IPART: Data revised in 2014-15. See notes
Note on S54: IPART: Data revised in 2014-15. See notes
Note on U54: IPART: Data revised in 2014-15. See notes
Note on W69: Value changed in 2016 upon clarification from Hunter Water. Originally reported entry was '-'
Note on Y85: Performance has been revised relative to Table 7.2 of Hunter Water's 2014-15 Compliance and Performance Report, and data published in National Performance Report 2014-14: urban water utilities, Part B - retrieved from: http://www.bom.gov.au/watee to clarifications in relation to the definitions of sewage treatment levels.
Note on Y86: Performance has been revised relative to Table 7.2 of Hunter Water's 2014-15 Compliance and Performance Report, and data published in National Performance Report 2014-14: urban water utilities, Part B - retrieved from: http://www.bom.gov.au/watee to clarifications in relation to the definitions of sewage treatment levels.

## Customers
Chapter 4: Customers
Indicator/System Performance Standard |  |  |  | Utility | 2005/06 |  | 2006/07 |  | 2007/08 |  | 2008/09 |  | 2009/10 |  | 2010/11 |  | 2011/12 |  | 2012/13 |  | 2013/14 |  | 2014/15 |  | 2015/16 |  | Notes/Comments
Type | NEW No. | Prev. No. | Description
IPART | C1 | C1 | The percentage of complaints resolved within 10 business days | Sydney Water | 89.72% | 24 | 89.48% | 39 | 89.86% | 39 | 91.02% | 29 | 86.29% | 46 | 85.6% | 49 | 86.3% | 48 | 90.2% | 66 | 91.3% | 93 | 91.3% | 119 | 90% | 119
IPART | C2 | C2 | Percent of calls abandoned | Sydney Water | - |  | - |  | - |  | - |  | - |  | - |  | - |  | 2.2% | 66 | 2.8% | 93 | 2.9% | 103 | 3.2% | 112
IPART | C3 | C3 | Percent of metered accounts of customers that receive a bill not based on a business meter read for one year | Sydney Water | - |  | - |  | - |  | - |  | - |  | - |  | - |  | 0.5% | 66 | 0.5% | 93 | 0.5% | 103 | 0.5% | 112
IPART | - | C4 | Number per 1000 properties of contacts received by water utility that are requests for instalment or deferred payment plans | Sydney Water | 50.08 | 39 | 61.32 | 39 | 64 | 39 | 79.39 | 29 | 89.6 | 46 | 88.6 | 49 | 86.4 | 48 | 94.7 | 66
IPART | - | C5 (S) | The total number of residential customers with continuing instalment plans with durations greater than 3 months. | Sydney Water | [14 empty] | 12192 | 66
IPART | - | C6 (S) | The total number of non-residential customers with continuing instalment plans with durations greater than 3 months | Sydney Water | [14 empty] | 560 | 66
IPART | - | C7 | Percent of residential customers on instalment plans | Sydney Water | [10 empty] | - |  | - |  | 1.8% | 66
IPART | - | C8 | Percent of non-residential customers on instalment plans | Sydney Water | [10 empty] | - |  | - |  | 0.8% | 66
IPART | - | C9 | Number of customers receiving payment assistance vouchers or payment assistance scheme credits | Sydney Water | - |  | - |  | - |  | 2430 | 66 | 3016 | 66 | 3203 | 66 | 3184 | 66 | 2422 | 66
IPART | - | C10 | Value of payment assistance vouchers or payment assistance scheme credits provided to customers | Sydney Water | 324926 | 25 | 375319 | 39 | 379343 | 39 | 438777 | 29 | 596710 | 46 | 692487 | 49 | 720748 | 66 | 789919 | 66
IPART | C4 | C11 | The total number of residential customers disconnected for non-payment of amounts owed to the utility. | Sydney Water | 0 |  | 0 | 39 | 0 | 39 | 0 | 29 | 0 | 46 | 0 | 49 | 0 | 48 | 0 | 66 | 0 | 93 | 0 | 103 | 0 | 121
IPART | - | C11 | The total number of residential customers disconnected for non-payment of amounts owed to the utility (per 1000 properties) | Sydney Water | 0 | 39 | 0 | 39 | 0 | 39 | 0 | 29 | 0 | 46 | - |  | - |  | -
IPART | C5 | C12 | The total number of non-residential customers disconnected for non-payment of amounts owed to the utility. | Sydney Water | 0 | 39 | 0 | 39 | 0 | 39 | 0 | 29 | 2 | 46 | 0 | 49 | 0 | 48 | 0 | 66 | 0 | 93 | 0 | 103 | 0 | 112
IPART | C6 | C13 | Total number of residential customers on whom water flow restrictions have been imposed | Sydney Water | 1777 | 39 | 2385 | 39 | 3493 | 39 | 3881 | 29 | 4720 | 46 | 5792 | 49 | 5241 | 48 | 6514 | 66 | 8226 | 93 | 6049 | 103 | 6298 | 112 | Sydney Water only restricts a customer due to non-payment of an account.
IPART | - | C13 | Total number of residential customers on whom water flow restrictions have been imposed (per 1000 properties) | Sydney Water | 1.2 | 39 | 1.5 | 39 | 2.17 | 39 | 2.39 | 29 | 2.89 | 46
IPART | C7 | C14 | Total number of non-residential customers on whom water flow restrictions have been imposed | Sydney Water | 102 |  | 109 |  | 216 |  | 286 | 29 | 363 | 46 | 284 | 49 | 262 | 48 | 420 | 66 | 517 | 93 | 319 | 103 | 222 | 112
IPART | C8 | - | Number of residential customers per 1000 residential properties experiencing financial difficulty who are being assisted through the water utility's hardship program or payment plans | Sydney Water | [16 empty] | 12.2 | 93 | 10.6 | 103 | 9.1 | 112
IPART | C9 a | - | Percentage of residential customers in C8 who are not meeting ongoing water and sewerage costs (debt increasing) | Sydney Water | [16 empty] | 18% | 93 | 17.4% | 103 | 19.3% | 112
IPART | C9 b | - | Percentage of residential customers in C8 who are covering ongoing water and sewerage costs (debt stable) | Sydney Water | [16 empty] | 18% | 93 | 18.6% | 103 | 19.9% | 112
IPART | C9 c | - | Percentage of residential customers in C8 who are covering ongoing costs and portion of arrears (debt reducing) | Sydney Water | [16 empty] | 64% | 93 | 64% | 103 | 60.8% | 112
IPART | C10 a | - | Percentage of residential customers in C8 who pay by payment plan | Sydney Water | [16 empty] | 93.2% | 93 | 90.1% | 103 | 90.1% | 112
IPART | C10 b | - | Percentage of residential customers in C8 who pay by Centrepay | Sydney Water | [16 empty] | 4.7% | 93 | 4.4% | 103 | 3.8% | 112
IPART | C11 a | - | Break up by percentage of residential customers who no longer meet C8 by exiting the water utility's hardship program or payment plans because they have paid off their outstanding debt | Sydney Water | [16 empty] | 83% | 93 | 85.5% | 103 | 91.4% | 112
IPART | C11 b | - | Break up by percentage of residential customers who no longer meet C8 by exiting the water utility's hardship program or payment plans because they have been flow restricted | Sydney Water | [16 empty] | 11.7% | 93 | 8.8% | 103 | 0.9% | 112
IPART | C11 c | - | Break up by percentage of residential customers who no longer meet C8 by exiting the water utility's hardship program or payment plans because other | Sydney Water | [16 empty] | 5.3% | 93 | 5.7% | 103 | 7.6% | 112
IPART | C12 | C12 | The number of non-residential customers affected by an unplanned water interruption of greater than 1 hour duration. | Sydney Water | [20 empty] | 22523 | 112 | New indicator implemented from 2015-16
IPART | C13 | C13 | The average duration of unplanned interruptions experienced by non-residential customers. | Sydney Water | [20 empty] | 2:49 mins | 112 | New indicator implemented from 2015-16
IPART | - | C14 | Total number of non-residential customers on whom water flow restrictions have been imposed (per 1000 properties) | Sydney Water | 0.82 | 39 | 0.86 | 39 | 1.68 | 39 | 2.17 | 29 | 2.65 | 46
IPART | C1 | C1 | The percentage of complaints resolved within 10 business days | Hunter Water | [14 empty] | 81% | 63 | 88% | 94 | 93% | 102 | 95% | 110
IPART | C2 | C2 | Percent of calls abandoned | Hunter Water | [6 empty] | 3.3% | 63 | 4.1% | 63 | 5.4% | 63 | 6.1% | 63 | 4.7% | 63 | 3.5% | 94 | 3.6% | 102 | 4.1% | 110
IPART | C3 | C3 | Percent of metered accounts of customers that receive a bill not based on a business meter read for one year | Hunter Water | - |  | - |  | - |  | - |  | - |  | - |  | - |  | 0.18% | 63 | 3.05% | 94 | 4.04% | 102 | 4.97% | 120 | Hunter Water updated its reporting procedure in the 2013/14 period and previous data is not comparable.
IPART | - | C4 | Number per 1000 properties of contacts received by water utility that are requests for instalment or deferred payment plans. | Hunter Water | - |  | - |  | - |  | - |  | - |  | - |  | - |  | 106.5 | 63
IPART | - | C7 | Percent of residential customers on instalment plans | Hunter Water | - |  | - |  | - |  | - |  | - |  | - |  | - |  | 2.48% | 63
IPART | - | C8 | Percent of non-residential customers on instalment plans | Hunter Water | - |  | - |  | - |  | - |  | - |  | - |  | - |  | 0.24% | 63
IPART | - | C9 | Number of customers receiving payment assistance vouchers or payment assistance scheme credits | Hunter Water | 426 | 34 | 434 | 34 | 425 | 34 | 429 | 76 | 569 | 76 | 620 | 76 | 559 | 76 | 962 | 63 | [6 empty] | Hunter Water released a new Hardship Policy in 2012/13. This saw an increase in the number of customers who were entitled to payment assistance.
IPART | - | C10 | Value of payment assistance vouchers or payment assistance scheme credits provided to customers | Hunter Water | 46600 | 34 | 53300 | 34 | 52975 | 34 | 53550 | 34 | 74475 | 34 | 96050 | 34 | 86550 | 34 | 121803 | 63 | [6 empty] | Hunter water released a new Hardship Policy in 2012/13. This saw an increase in the number of customers who were entitled to payment assistance.
IPART | C4 | C11 | The total number of residential customers disconnected for non-payment of amounts owed to the utility | Hunter Water | - |  | - |  | - |  | - |  | - |  | - |  | - |  | 0 | 63 | 0 | 94 | 0 | 102 | 0 | 110
IPART | C5 | C12 | The total number of non-residential customers disconnected for non-payment of amounts owed to the utility | Hunter Water | - |  | - |  | - |  | - |  | - |  | - |  | - |  | 0 | 63 | 0 | 94 | 0 | 102 | 0 | 110
IPART | C6 | C13 | Total number of residential customers on whom water flow restrictions have been imposed | Hunter Water | - |  | - |  | - |  | - |  | - |  | - |  | - |  | 1118 | 63 | 1381 | 94 | 1704 | 102 | 1512 | 110 | The 2013-14 report include data for previous 5 years.
IPART | C7 | C14 | Total number of non-residential customers on whom water flow restrictions have been imposed | Hunter Water | - |  | - |  | - |  | - |  | - |  | - |  | - |  | 74 | 0 | 49 | 94 | 32 | 102 | 40 | 110
IPART | C8 | - | Number of residential customers per 1000 residential properties experiencing financial difficulty who are being assisted through the water utility's hardship program or payment plans | Hunter Water | [16 empty] | 18.8 | 94 | 15.1 | 102 | 16.5 | 110
IPART | C9 a | - | Percentage of residential customers in C8 who are not meeting ongoing water and sewerage costs (debt increasing) | Hunter Water | [16 empty] | 24.4% | 94 | 19.4% | 102 | 25.8% | 110
IPART | C9 b | - | Percentage of residential customers in C8 who are covering ongoing water and sewerage costs (debt stable) | Hunter Water | [16 empty] | 36.8% | 94 | 37.5% | 102 | 38.8% | 110
IPART | C9 c | - | Percentage of residential customers in C8 who are covering ongoing costs and portion of arrears (debt reducing) | Hunter Water | [16 empty] | 38.8% | 94 | 43.1% | 102 | 35.4% | 110
IPART | C10 a | - | Percentage of residential customers in C8 who pay by payment plan | Hunter Water | [16 empty] | 88.1% | 94 | 86.6% | 102 | 87.5% | 110
IPART | C10 b | - | Percentage of residential customers in C8 who pay by Centrepay | Hunter Water | [16 empty] | 6.8% | 94 | 9.8% | 102 | 8.7% | 110
IPART | C11 a | - | Break up by percentage of residential customers who no longer meet C8 by exiting the water utility's hardship program or payment plans because they have paid off their outstanding debt | Hunter Water | [16 empty] | 66.7% | 94 | 55% | 102 | 41.8% | 110
IPART | C11 b | - | Break up by percentage of residential customers who no longer meet C8 by exiting the water utility's hardship program or payment plans because they have been flow restricted | Hunter Water | [16 empty] | 8.5% | 94 | 8.8% | 102 | 11.6% | 110
IPART | C11 c | - | Break up by percentage of residential customers who no longer meet C8 by exiting the water utility's hardship program or payment plans because other | Hunter Water | [16 empty] | 24.8% | 94 | 36.2% | 102 | 46.6% | 110
IPART | - | 2. PF (a) | The volume of water taken in excess of access licence conditions under the Water Management Act 2000 (in mega litres (ML) and number of licences and licence breaches involved | WaterNSW (State Water)
|  |  | Volume of water taken in excess of access licence conditions (ML) | WaterNSW (State Water) | 3811.3 | 12 | 7355 | 68 | 7489 | 13 | 3258 | 14 | 2748 | 15 | 1792 | 16 | 6393 | 17 | 1066.6 | 18
|  |  | Number of licences and licence breaches involved | WaterNSW (State Water) | 44 | 12 | 162 | 68 | 91 | 13 | 114 | 14 | 114 | 15 | 48 | 16 | 49 | 17 | 67 | 18
IPART | - | 2. PF (b) | Value of penalties imposed by State Water for taking of water in excess of licence conditions under the Water Management Act 2000 or the Water Act 1912 | WaterNSW (State Water) | 1230.15 | 12 | 0 | 68 | 0 | 13 | 0 | 14 | 0 | 15 | 0 | 16 | 0 | 17 | 0 | 18
IPART | - | 2. PF (c) | Volume of penalties imposed by State Water for taking water in excess of access licence conditions under the Water Management Act 2000 (ML) | WaterNSW (State Water) | 1360 | 12 | 319.5 | 68 | 314 | 13 | 0 | 14 | 0 | 15 | 0 | 16 | 0 | 17 | 0 | 18
IPART | - | 2. PF (d) | Number of water supply works audited for compliance with metering conditions and the proportion of those works that comply with metering conditions | WaterNSW (State Water) | [22 empty] | Reporting of this indicator commenced in 2007/08. This Indicator ceased to exist in April 2012.
|  |  | Number audited for compliance | WaterNSW (State Water) | [6 empty] | 0 | 14 | 0 | 15 | 4601 | 16
|  |  | Number that comply with conditions | WaterNSW (State Water) | [6 empty] | - |  | - |  | 0.002% | 16
IPART | - | 2. PF (e) | Number of “alleged breach reports” forwarded to the NSW Office of Water (NOW) | WaterNSW (State Water) | 2 | 12 | - |  | - | 13 | 8 | 14 | 73 | 15 | 58 | 16 | 57 | 17 | 33 | 18 | [6 empty] | NOW was previously known as the Department of Water and Energy.
IPART | - | 2. PF (f) | Number of licences and entitlements suspended under the Water Management Act 2000 or the Water Act 1912 | WaterNSW (State Water) | 0 | 12 |  |  | 0 | 13 | 0 | 14 | 0 | 15 | 0 | 16 | 11 | 17 | 21 | 18 | 43 | 95 | 20 | 106 | 16 | 116
IPART | - | 2. PF (g) | Number of approvals suspended under the Water Management Act 2000 | WaterNSW (State Water) | 0 | 12 |  |  | 0 | 13 | 0 | 14 | 0 | 15 | 0 | 16 | 0 | 17 | 0 | 18 | 0 | 95 | 0 | 106 | 0 | 116
NWI | C13 | C13 | Total water and sewerage complaints (no. per 1000 properties) | Sydney Water | - |  | 4.3 | 49 | 7.7 | 49 | 6 | 49 | 4.1 | 49 | 3.4 | 49 | 3.5 | 48 | 3.9 | 66 | 3.2 | 93 | 2.7 | 119 | 2.6 | 119
NWI | C14 | C14 | Percentage of calls answered by an operator within 30 seconds | Sydney Water | 84.26% | 39 | 83.22% | 39 | 88.48% | 39 | 84.7% | 66 | 88.9% | 66 | 79.3% | 66 | 86.2% | 66 | 86% | 66 | 82.5% | 93 | 79.2% | 103 | 73% | 112 | Sydney Water attributed the lowering of this value to a shift in focus from grade of service to customer experience. Staff are now encouraged to engage more with customers, resulting in an increase in average phone call length to five minutes accompanied by an increase in first call resolutions.
NWI | C13 | C13 | Total Water and sewerage complaints (no. per 1000 properties) | Hunter Water | [6 empty] | 7.35 | 63 | 8.21 | 63 | 7.62 | 63 | 7.56 | 63 | 7.05 | 67 | 6.7 | 94 | 6.31 | 102 | 4.77 | 110 | The definition of this indicator changed in 2008/09. Data not comparable prior to 2008/09.
NWI | C14 | C14 | Percentage of calls answered by an operator within 30 seconds | Hunter Water | 68 | 22 | 61 | 22 | 56 | 22 | 72 | 63 | 70 | 63 | 60 | 63 | 71 | 63 | 79 | 63 | 71 | 94 | 70 | 102 | 71 | 110
End of Customers data
End of Customer Performance data
Note on W25: There are an additional 2.1% of customers who received payment assistance scheme credits or where no payments had been made due to recent entry into the hardship program. (Sydney Water)
Note on M60: Audits commenced in 2009/10. Audits to be 4 year cyclic.
Note on K62: Reporting commenced in 2008/09.
Note on W67: IPART: Revised in 2014-15 data reporting period. See reference 102.

## References
# | TRIM Reference |  | Date | Title | # | TRIM Reference |  | Date | Title
| Doc # | folder # |  |  |  | Doc # | folder #
1 | D06/7784 | 06/224-1 | 2006-08-07 | Hunter Water Corporation Operating Licence Performance to 30 June 2006 | 63 | D13/30951 | 12/372 | 2013-09-01 | Hunter Water Corporation Compliance and Performance Report 2012-13
2 | D07/12421 | 06/224-1 | 2007-07-19 | Hunter Water Corporation Operating Licence Performance to 30 June 2007 | 64 | D13/35433 | 10/383 | 2013-10-01 | Sydney Water Operating Licence Environment Report Environmental Indicators Report 2012-13
3 | D08/9068 | 06/224-2 | 2008-08-14 | Hunter Water Corporation Operating Licence Performance to 30 June 2008 | 65 | D13/30424 | 10/383 | 2013-09-01 | Sydney Water Operating Licence 2010-2015 System Performance Standards Report 2012-13 (Schedule B)
4 | D09/8274 | 06/224-3 | 2009-08-10 | Hunter Water Corporation Operating Licence Performance to 30 June 2009 | 66 | D13/30424 | 10/383 | 2013-09-01 | Sydney Water Operating Licence 2010-2015 Performance Indicators Report 2012-13 (Schedule C)
5 | D10/9897 | 10/39 | 2010-07-30 | Hunter Water Corporation Operating Licence Performance to 30 June 2010 | 67 | D14/774 | 13/226 | 2013-11-11 | Email - Hunter Water Corporation - to IPART Secretariat
6 | D11/12640 | 10/590 | 2011-07-28 | Hunter Water Corporation Operating Licence Performance to 30 June 2011 | 68 | - | - | 2007-08-31 | State Water Corporation Report to IPART under the Operating Licence 31 August 2007
7 | D12/13376 | 06/224-4 | 2012-07-27 | Hunter Water Corporation Operating Licence Performance to 30 June 2012 | 69 | D08/14502 | 05/321-3 | 2008-09-30 | Sydney Water Operating Licence Compliance Report 2007-08 - Schedule 3 Environmental Performance Indicators
8 | D13/26622 | 12/372 | 2013-07-25 | Hunter Water Corporation Operating Licence Performance to 30 June 2013 | 70 | - | - | 2013-11-27 | 2013 Audit of the Sydney Drinking Water Catchment: Volume 1 - Main Report
9 | - | - | - | Sydney Catchment Authority Annual Water Quality Monitoring Report 2009-10 Appendix A | 71 | - | - | 2010-11-01 | 2010 Audit of the Sydney Drinking Water Catchment: Volume 1 - Main Report
10 | D11/21125 | 11/414 | 2011-11-30 | Sydney Catchment Authority Annual Water Quality Monitoring Report 2010-11 | 72 | - | - | 2007-12-01 | 2007 Audit of the Sydney Drinking Water Catchment
11 | - | - | - | Sydney Catchment Authority Annual Water Quality Monitoring Report 2011 -12 Appendices | 73 | - | - | 2005-12-01 | 2005 Audit of the Sydney Drinking Water Catchment
12 | D06/8608 | 06/379 | 2006-09-01 | State Water Corporation Report to IPART under the Operating Licence 1 September 2006 | 74 | D14/9670 | 13/226 | 2014-03-07 | Sydney Catchment Authority response to review of performance indicator data
13 | D08/9838 | 08/450 | 2008-09-01 | State Water Corporation Report to IPART under the Operating Licence 1 September 2008 | 75 | D14/9672 | 13/226 | 2014-03-11 | Sydney Water Corporation response to review of performance indicator data
14 | D11/11206 | 09/184 | 2009-09-01 | State Water Corporation Report to IPART under the Operating Licence 1 September 2009 | 76 | D14/9671 | 13/226 | 2014-03-10 | Hunter Water Corporation response to review of performance indicator data
15 | D11/11098 | 10/259 | 2010-09-01 | State Water Corporation Report to IPART under the Operating Licence 1 September 2010 | 77 | D14/9677 | 13/226 | 2014-03-12 | State Water Corporation response to review of performance indicator data
16 | D12/271 | 08/450 | 2011-09-01 | State Water Corporation Report to IPART under the Operating Licence 1 September 2011 | 78 | - | - | - | Sydney Catchment Authority Annual Water Quality Monitoring Report 2005-06
17 | D12/16573 | 12/135 | 2012-09-01 | State Water Corporation Report to IPART under the Operating Licence 1 September 2012 | 79 | - | - | - | Sydney Catchment Authority Annual Water Quality Monitoring Report 2006-07
18 | D13/30748 | 13/345 | 2013-09-01 | State Water Corporation Report to IPART under the Operating Licence 1 September 2013 | 80 | - | - | - | Sydney Catchment Authority Annual Water Quality Monitoring Report 2007-08
19 | D13/40988 | 12/374 | 2013-11-27 | Sydney Catchment Authority Annual Water Quality Monitoring Report 2012‐13 | 81 | - | - | - | Sydney Catchment Authority Annual Water Quality Monitoring Report 2008-09
20 | - | - | 2014-04-02 | National Performance Report 2012-13: Urban Water Utilties PART B: Full data set | 82 | - | - | - | Sydney Catchment Authority Annual Water Quality Monitoring Report 2009-10
21 | - | - | 2013-03-01 | National Performance Report 2011-12: Urban Water Utilities PART B: Full data set | 83 | - | - | - | Sydney Catchment Authority Annual Water Quality Monitoring Report 2010-11 Appendices
22 | - | - | 2012-04-01 | National Performance Report 2010-11 Urban Water Utilities PART B: Spreadsheet of all data reported | 84 | - | - | - | Sydney Catchment Authority Annual Water Quality Monitoring Report 2011-12
23 | - | - | - | Recalculated from data in National performance data base 2012-13 (Calculation in cell) | 85 | - | - | - | Sydney Catchment Authority Annual Water Quality Monitoring Report 2005-06 Appendices
24 | D06/8593 | 05/321-1 | 2006-09-01 | Sydney Water Operating Licence Compliance Report 1 July 2005 to 30 June 2006 | 86 | - | - | - | Sydney Catchment Authority Annual Water Quality Monitoring Report 2006-07 Appendices
25 | D06/8593 | 05/321-1 | 2006-09-01 | Sydney Water Water Conservation and Recycling Implementation Report 2005-2006 | 87 | - | - | - | Sydney Catchment Authority Annual Water Quality Monitoring Report 2007-08 Appendices
26 | D07/11179 | 05/321-1 | 2007-09-01 | Sydney Water Compliance Reports for 2005-2010 Operating Licence | 88 | - | - | - | Sydney Catchment Authority Annual Water Quality Monitoring Report 2008-09 Appendices
27 | D07/13325 | 05/321-1 | 2007-09-27 | Sydney Water Operating Licence Compliance Report Schedule 3 Environmental Performance Indicators 2006-07 | 89 | - | - | - | Sydney Catchment Authority Annual Water Quality Monitoring Report 2012-13 Appendices
28 | D09/8501 | 09/183 | 2009-09-01 | Hunter Water Annual Operating Licence Report System Performance Standards and Indicators 2008-09 | 90 | D14/10757 | 13/226 | 2014-03-28 | Email - Sydney Catchment Authority - to IPART Secretariat
29 | D09/10590 | 05/321-3 | 2009-09-01 | Sydney Water Operating Licence Compliance Report Annual Report 2008-09 | 91 | D14/10765 | 13/226 | 2014-03-28 | Email - Hunter Water Corporation - to IPART Secretariat
30 | D09/10171 | 05/321-1 | 2009-09-30 | Sydney Water 2005-2010 Operating Licence Environmental Compliance Reports | 92 | D15/3203 | 13/351 | 2015-02-13 | Sydney Water Operating Licence 2010-2015 Performance Compliance Report 2013-14 System Performance Standards Report (Schedule B)
31 | D10/11533 | 10/258 | 2010-09-01 | Hunter Water Service Quality and System Performance Report 2009-10 | 93 | D15/3203 | 13/351 | 2015-02-13 | Sydney Water Operating Licence 2010-2015 Performance Indicators Report 2013-14
32 | D10/11533 | 10/258 | 2010-09-01 | Hunter Water Catchment Report 2009-10 | 94 | LC14/11 | 15/147 | 2014-09-01 | Hunter Water Compliance and Performance Report 2013-14
33 | D10/11533 | 10/258 | 2010-09-01 | Hunter Water Consultative Forum Report 2009-10 | 95 | LC14/12 | 15/147 | 2014-09-01 | State Water Corporation Report to IPART under the Operating Licence 1 September 2014
34 | D10/11533 | 10/258 | 2010-09-01 | Hunter Water Customer Service Report 2009-10 | 96 | D15/916 | 15/147 | 2014-10-01 | Sydney Water Operating Licence Environment Report Environmental Indicators Report 2013-14
35 | D10/11533 | 10/258 | 2010-09-01 | Hunter Water Environmental Performance Indicators Report 2009-10 | 97 | LC14/10 | 15/147 | 2014-09-01 | Sydney Water Operating Licence Water Efficiency Report - 1 September Report 2013-14
36 | D10/11533 | 10/258 | 2010-09-01 | Hunter Water Integrated Water Resources (H250) Plan Report 2009-10 | 98 | D15/3203 | 13/351 | 2015-02-13 | Correspondence (Letter) Sydney Water to IPART
37 | D09/8501 | 09/183 | 2009-09-01 | Hunter Water Annual Operating Licence Report System Performance Standards and Indicators 2008-09 | 99 | - | - | 2015-01-23 | Sydney Catchment Authority Annual Water Quality Monitoring Report 2013-14 & Appendices
38 | D09/8502 | 09/183 | 2009-09-01 | Hunter Water Annual Operating Licence Report Environmental Performance Indicators 2008/09 | 100 | D15/5555 | 15/147 | 2014-10-01 | National Performance Report NWI Data provided to IPART annual reporting
39 | D14/9392 | 05/321-2 | 2008-09-01 | Sydney Water Operating Licence Compliance Report Annual Report 2007-08 | 101 | D15/5398 | 15/147 | 2015-03-12 | Email - Sydney Water Corporation to IPART Secretariat
40 | - | - | 2010-09-10 | Sydney Water Water Conservation and Recycling Implementation Report 2009-10 | 102 |  |  | 2015-09-01 | Hunter Water Compliance and Performance Report 2014-15
41 | - | - | 2010-10-01 | Sydney Water Operating Licence Compliance Report Schedule 3: Environmental Performance Indicators 2009-10 | 103 |  |  | 2015-11-24 | Sydney Water Operating Licence 2010-2015 Performance Indicators Report 2014-15
42 | D12/7513 | 10/383 | 2010-10-04 | Sydney Water Operating Licence Environment Report - Environmental Indicators Report 2010-11 | 104 |  |  | 2015-09-01 | Sydney Water Operating Licence 2010-2015 System Performance Standards Report 2014-15 (Schedule B)
43 | D12/16879 | 11/247 | 2011-09-01 | Sydney Water Water Efficiency Report 2010-11 (Schedule D) | 105 |  |  | 2015-10-01 | Sydney Water Operating Licence Environmental Indicators Report 2014-15
44 | - | - | - | Sydney Water Water Efficiency Report 2012-13 | 106 |  |  | 2015-09-01 | WaterNSW Report to IPART under the Operating Licence 2013-18 for State Water
45 | D12/18166 | 12/131 | 2012-10-01 | Sydney Water Operating Licence Environment Report - Environmental Indicators Report 2011-12 | 107 |  |  | 2015-10-30 | National Performance Report NWI Data provided to IPART annual reporting
46 | D11/8809 | 10/257-1 | 2010-09-01 | Sydney Water Operating Licence Compliance Report Annual Report 2009-10 | 108 |  |  | - | WaterNSW Annual Water Quality Monitoring Report 2014-15
47 | D11/8876 | 10/257-2 | 2010-09-08 | Sydney Water Water Conservation and Recycling Implementation Report 2009-10 | 109 |  |  | - | WaterNSW Annual Water Quality Monitoring Report 2014-15 Appendices
48 | D12/18159 | 12/131 | 2012-08-30 | Sydney Water Operating Licence 2010-2015 Performance Indicators Report 2011-12 (Schedule C) | 110 |  |  | 2016-09-01 | Hunter Water Compliance and Performance Report 2015-16
49 | D12/16879 | 11/247 | 2011-08-31 | Sydney Water Operating Licence 2010-2015 Performance Indicators Report 2010-11 (Schedule C) | 111 |  |  | 2016-09-01 | Sydney Water Environment Compliance and Performance Report 2015-16
50 | D11/8817 | 10/257-1 | 2010-09-01 | Sydney Water Folio of Progress Water Pressure Standard | 112 |  |  | 2016-09-01 | Sydney Water operating Licence 2015-2020 Performance Indicators Report 2015-16
51 | D12/18159 | 12/131 | 2012-08-31 | Sydney Water Operating Licence 2010-2015 Compliance Report - System Performance Standards Report 2011-12 (Schedule B) | 113 |  |  | 2016-09-01 | Sydney Water Operating Licence 2015-2020 System Performance Standards Report 2015-16
52 | D11/8817 | 10/257-1 | 2010-09-01 | Sydney Water Folio of Progress Water Continuity Standard | 114 |  |  | 2016-09-01 | Sydney Water Water Conservation Report 2015-16
53 | D12/16879 | 11/247 | 2011-09-01 | Sydney Water Operating Licence 2010-2015 System Performance Standard Report 2010-11 (Schedule B) | 115 |  |  | 2016-09-01 | WaterNSW 2015-16 water resource indicators
54 | D11/8817 | 10/257-1 | 2010-09-01 | Sydney Water Folio of Progress Sewage Overflow Standard | 116 |  |  | 2016-09-01 | WaterNSW Report to IPART under the Operating Licence 2013-18 for Non-Sydney Catchment Functions
55 | D11/8817 | 10/257-1 | 2010-09-01 | Sydney Water Folio of Progress Response Time for Water Main Breaks | 117 |  |  | 2016-11-01 | WaterNSW Annual Water Quality Monitoring Report 2015-16
56 | D11/20672 | 11/249 | 2011-09-01 | Hunter Water Service Quality and System Performance Report 2010-11 | 118 |  |  | 2016-11-01 | WaterNSW Annual Water Quality monitoring Report 2015-16 Appendices
57 | D13/3895 | 12/133 | 2012-09-01 | Hunter Water Service Quality and System Performance Report 2011-12 | 119 |  |  | 2016-12-01 | Email from Sydney Water to IPART
58 | D08/10851 | 08/127-1 | 2008-09-01 | Hunter Water Corporation System Performance Standards and Service Quality and System Performance Indicators - September 2008 | 120 |  |  | 2016-12-01 | Email from Hunter Water to IPART
59 | D07/12379 | 06/224-1 | 2007-08-01 | Hunter Water System Performance Schedule 4 2006-07 Report to IPART August 2007 | 121 |  |  | 2017-01-01 | Email from IPART to Sydney Water
60 | D08/10853 | 08/127-1 | 2008-09-01 | Hunter Water Corporation Environment Performance Indicators - September 2008 | 122
61 | D11/20672 | 11/249 | 2011-09-01 | Hunter Water Environmental Performance Indicators Report 2010-11 | 123
62 | D13/3895 | 12/133 | 2012-08-01 | Hunter Water Corporation Environmental Performance Indicators Report 2011-12 | 124
End of reference list
Note on K11: Currently available at: http://www.parliament.nsw.gov.au/prod/la/latabdoc.nsf/062281a7012b5820ca257020000a3058/dd593c6881c3b4a6ca257c4600814ee6?OpenDocument&Highlight=0,catchment*,audit*